## Intro
Toronto 2030 District
Capital Cost Calculations: Building Level
Revision Date | 2024-04-24
Pathways Project |  | The Pathways Project aims to describe strategies to decarbonize districts while maintaining overall building occupancies and uses.
Pathways Cost Estimation (This Spreadsheet) |  | This spreadsheet quantifies capital costs required to modify buildings to enable them to operate using net zero carbon technologies: Electric resistance, Air-source heat pumps, ground source heat pumps, hydrogen, and Deep Energy Retrofits (DER). Target audiences using conclusions of the spreadsheet include policy makers, real estate portfolio owners/managers, and advisors to these groups.
Changing Inputs |  | Users who change spreadsheet inputs should have appropriate subject matter expertise and apply edits based on appropriate data that is applicable to the context. Default inputs and assumptions in this spreadsheet were informed by subject matter expert input relevant to Toronto's 2030 District. User-specific situations may not be addressed by default inputs alone.
Method |  | The methodology applied to this tool is found in the following Net Zero Pathways Tool Guide and Methodology link: https://2030districts.org/toronto/wp-content/uploads/sites/28/Toronto-2030-District-Net-Zero-Buildings-Pathways-Tool-FINAL-Guide-and-Methodology-May-2024.pdf. Default Gas and Electrical Use data was collected in a previous 2030 Project (https://www.toronto2030platform.ca/), then divided into occupancy types, and further divided into archetypes representing the most common building energy use signatures.
Colour Legend for Cells | Meaning | Colour
User-Changeable
| Non-Changeable: | Calculation Outputs / Information
| Flagged Values: | Includes user notes with explanations as to why the values are flagged
Net-Zero Building Pathways Tool Tabs
TAB GROUPING | TABS | CONTENT
General Tabs | [Intro] | High-level instruction, background, and navigation for the tool
| [Global Inputs] | Input assumption applied to multiple tabs within the tool
| [Building Typology] | Inputs and outputs on building types, baseline energy consumption, and system sizing
| [System Descriptions] | Descriptions of the default inputs used for the tools electrical, mechanical, and building envelope calculations
System Retrofit Tabs (Fuel Switching) | [FS - Unitary Capital] | Input tab for unitary capital replacement costs and fixed electrical and equipment capital costs of each fuel-switching option
| [FS – Capital Output] | Output tab for the calculated capital replacement costs of each fuel-switching option
| [FS - Operational] | Input tab about for the annual utility cost of each fuel-switching option
| [FS - Business Case] | Output tab calculating the total retrofit cost and comparing each option to the base case
| [FS – Graphical Analyses] | Provides graphical representations of fuel switching data
Envelope Replacement Tabs (Efficiency) | [Efficiency] | Inputs and outputs on building form, massing, current envelope measures, “business-as-usual” envelope-replacement measures, and deep energy retrofit (DER) replacement measures
Workbook Flow
Visual Description:
· | Colours used follow the tab groupings
· | The arrows describe how each tab is related and order of operations
[Global Inputs]
[Building Typology]
[FS – Capital Output]
[FS - Operational]
[Business Case]
[Efficiency]
[FS - Unitary Capital]

## Global Inputs
Toronto 2030 District
Conversions
Conversion Factors
| m² to ft² | 10.7639
| kW(th) to MBH | 3.415
| MBH to Tons | 0.083333
Global Inputs
| List of Baseline Primary Heating Sources | [7 empty] | INPUT NOTES
| 1 | Gas | [6 empty] | Building types include boilers, MUA, RTU's, etc. that rely on gas
| 2 | District | [6 empty] | Building types heated via District Energy (eg district steam, district hot water).
| 3 | Electric | [6 empty] | Building types use electric boilers/ radiators
4
5
6
7
8
9
| Construction Cost Item | Units | Percent on Construction | Multiplier |  |  |  |  | Input notes
| General Conditions (GC) | % of capital expenses | 10% | 0.1
| Contingency Costs (CC) | % of capital expenses | 20% | 0.2
| Project Management (PM) | % of capital expenses | 15% | 0.15
| Tax | % of capital expenses | 13% | 1.13
| Total Multiplier |  |  | 1.6385
| Utility Rate Input | Units | $/unit | ekWh/ unit | $/ekWh | Avg Fuel Emissions Intesity - Baseline Year to 2050 (g/ ekWh) | Baseline Fuel Carbon Price ($/ekWh) | Avg Fuel Carbon Price ($/ekWh) | Input notes
| Electricity | kWh | 0.16 | 1 | 0.16 | 50 | 0.004 | 0.015625 | Cost rate based on sample 2023/2024 commercial consumer all-in rate.
| Natural gas | m3 | 0.4 | 10.6398 | 0.037595 | 200 | 0.016 | 0.0625 | Cost rate based on sample 2023/2024 commercial consumer all-in rate.
| RNG | m3 | 1.08 | 10.6398 | 0.10151 | 50 | 0.004 | 0.015625 | Cost rate based on Enbridge website taken Feb 21, 2024. Emissions remain related to methane distribution leaks. Value is a placeholder. Refer to research by The Atmospheric Fund for context.
| Hydrogen | kWh | 0.19 | 1 | 0.19 | 71.4286 | 0.0057143 | 0.022321 | Cost rate input is needed. Emissions value input is needed - value varies considerably by source (eg: green vs blue vs gold hydrogen). Value shown here considers electricity as a source and 70% conversion efficiency (including storage, transmission).
| Heating Degree Days | [7 empty] | Input notes
| HDD 18C | 4300 | [6 empty] | Heating degree days for Toronto, Ontario
| Amortization Rate Input | [7 empty] | Input notes
| Interest Rate | 5%
| Amortization | Period (yrs) | Payment (% of capital) | [5 empty] | Input notes
| Like-for-Like Retrofit | 20 | 8.024% | [5 empty] | Cost is all ~20yr longevity equipment (eg boilers, electric boilers/ radiators).
| Hydrogen Conversion Retrofit | 30 | 6.505% | [5 empty] | Cost is ~15% ~50yr infrastructure (eg pipes), ~85% 10yr equipment (Hydrogen not yet commercially long-term proven). Amortization recovery capped at 30 yrs.
| Electric Resistance Retrofit | 30 | 6.505% | [5 empty] | Cost is ~25% ~50yr infrastructure (eg wires), ~25% 30yr infrastructure (eg transformers), ~50% 20yr equipment. Amortization recovery capped at 30 yrs.
| ASHP Retrofit | 30 | 6.505% | [5 empty] | Cost is ~50% ~50yr infrastructure (eg pipes), ~50% 20yr equipment (eg heat pumps). Amortization recovery capped at 30 yrs.
| ASHP w RNG Retrofit | 30 | 6.505% | [5 empty] | Cost is ~50% ~50yr infrastructure (eg pipes), ~50% 20yr equipment (eg heat pumps). Amortization recovery capped at 30 yrs.
| GSHP Retrofit | 30 | 6.505% | [5 empty] | Cost is ~80% ~50yr infrastructure (eg geoexchange field), ~20% 20yr equipment (eg heat pumps). Amortization recovery capped at 30 yrs.
| Carbon Price | $/ton | [6 empty] | Input notes
| Average | 312.5 | [6 empty] | Averaged over a 30 year period of financial analysis
| Current Year | $/ton
| 2024 | 80
| 2024 | 80
| 2025 | 95
| 2026 | 110
| 2027 | 125
| 2028 | 140
| 2029 | 155
| 2030 | 170
| 2031 | 185
| 2032 | 200
| 2033 | 215
| 2034 | 230
| 2035 | 245
| 2036 | 260
| 2037 | 275
| 2038 | 290
| 2039 | 305
| 2040 | 320
| 2041 | 335
| 2042 | 350
| 2043 | 365
| 2044 | 380
| 2045 | 395
| 2046 | 410
| 2047 | 425
| 2048 | 440
| 2049 | 455
| 2050 | 470
| 2051 | 485
| 2052 | 500
| 2053 | 515
| 2054 | 530
| 2055 | 545
Note on B12: User Note: This input is used to determine which heating source the building typologies referenced in this workbook are transitioning from. The empty spaces are included to add more than the initial 3 heating sources to the dropdown menu in the [Building Typology] tab.
Note on K12: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table
Note on K23: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table
Note on B25: User Note: Contingency costs should be inclusive of construction, design/scope, and any other relevant contingencies
Note on E28: User Note: Total Multiplier methodology is as folows (GC + CC + PM)*Tax
Note on E30: User Note: see Energy Star Portfolio Manager 'Thermal Conversions' Technical Reference
Note on G30: User Note: This value is from the baseline year to 2050. Refer to Canada's latest National Inventory Report for emission intensity values by fuel. Electricity values vary considerably by province, and occasionally by historic year. Fuel values vary modestly by province.
Note on K30: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table
Note on D31: User Note: Inclusive of carbon price and/or tax in the baseline year.
Note on D32: User Note: Inclusive of carbon price and/or tax in the baseline year.
Note on D33: User Note: Inclusive of carbon price and/or tax in the baseline year.
Note on D34: User Note: Inclusive of carbon price and/or tax in the baseline year.
Note on K36: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table
Note on K39: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table
Note on K42: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table
Note on K50: User Note: Use the input notes to justify or provide sourced of the assumed values in the adjacent table

## Building Typology
Toronto 2030 District
Occupancy & Sub-Categories | BUILDING POPULATION IN DISTRICT |  |  |  | BUILDINGS' PHYSICAL CHARACTERISTICS |  |  |  |  | BASELINE ENERGY CONSUMPTION | [7 empty] | SYSTEM SIZING
| Building Floor Area Distribution (by occupancy) | Total Building Gross Floor Area in District | Total Building Gross Floor Area in District | Zone Area | Avg Floorplate Conditioned Floor Area, GFA | Avg # Conditioned Floors | Avg Building Conditioned Gross Floor Area, GFA | Avg Building Conditioned Gross Floor Area, GFA | Avg # Suites/Units | Reference EUI (all fuels) | Baseline Primary Heating Source | Predicted District Energy Use | Calibrated Energy Use | Energy Allocation in District | Calibrated Natural Gas Use | Calibrated Natural Gas Use | Gas Allocation in District | Existing Plant Capacity - Space Heating |  |  |  | Existing Plant Capacity - Water Heating |  |  |  | Existing Plant Capacity - Space Cooling |  |  |  | Acheivable System Size Reduction - Space Heating | Acheivable System Size Reduction - Water Heating | Acheivable System Size Reduction - Space Cooling | Replacement Plant Capacity - Space Heating |  |  |  | Replacement Plant Capacity - Water Heating | Replacement Plant Capacity - Water Heating |  |  | Replacement Plant Capacity - Space Cooling | Replacement Plant Capacity - Space Cooling |  |  | MAU Replacement Size | RTU Replacement Size
Units | % | m² | ft² | % | m² | N/A | m² | ft² | N/A | ekWh/m² | N/A | eGWh | eGWh | % | eGWh | GJ | % | (W(th)/ft²) | kW(th) | MBH | Tons | (W(th)/ft²) | kW(th) | MBH | Tons | Existing Plant Capacity - Space Cooling | kW(th) | MBH | Tons | % | % | % | (W(th)/ft²) | kW(th) | MBH | Tons | (W(th)/ft²) | kW(th) | MBH | Tons | (W(th)/ft²) | kW(th) | MBH | Tons | CFM | Tons
OFFICE | 100% | 8671000 | 93333776.9 | [6 empty] | N/A |  | 2426.4926 | 2330 | 24.27% | 730 | 2628000 | 16.52%
Class 'A' - gas boiler | 46% | 3988660 | 42933537.374 | 12.76% | 1400 | 20 | 28000 | 301389.2 | 15.0695 | 268 | Gas | 1068.9609 | 1026.4523 | 10.69% | 501.194 | 1804298.5075 | 11.34% | 8 | 2411.1136 | 8233.9529 | 686.1627 | 0.72282 | 217.8506 | 743.9599 | 61.9967 | 9 | 2712.5028 | 9263.1971 | 771.9331 | 0% | 50% | 0% | 8 | 2411.1136 | 8233.9529 | 686.1627 | 0.36141 | 108.9253 | 371.98 | 30.9983 | 9 | 2712.5028 | 9263.1971 | 771.9331 | 0 | 0
Class 'A' - district heating/ cooling | 19% | 1647490 | 17733417.611 | 5.269% | 1400 | 20 | 28000 | 301389.2 | 15.0695 | 268 | District | 441.5273 | 423.9694 | 4.416% | 0 | 0 | 0% | 8 | 2411.1136 | 8233.9529 | 686.1627 | 0.72282 | 217.8506 | 743.9599 | 61.9967 | 9 | 2712.5028 | 9263.1971 | 771.9331 | 0% | 50% | 0% | 8 | 2411.1136 | 8233.9529 | 686.1627 | 0.36141 | 108.9253 | 371.98 | 30.9983 | 9 | 2712.5028 | 9263.1971 | 771.9331 | 0 | 0
Class 'A' - electric | 3% | 260130 | 2800013.307 | 0.8319% | 1400 | 20 | 28000 | 301389.2 | 15.0695 | 268 | Electric | 69.7148 | 66.9425 | 0.6973% | 0 | 0 | 0% | 8 | 2411.1136 | 8233.9529 | 686.1627 | 0.72282 | 217.8506 | 743.9599 | 61.9967 | 9 | 2712.5028 | 9263.1971 | 771.9331 | 0% | 50% | 0% | 8 | 2411.1136 | 8233.9529 | 686.1627 | 0.36141 | 108.9253 | 371.98 | 30.9983 | 9 | 2712.5028 | 9263.1971 | 771.9331 | 30000 | 0
Class 'B' & 'C' - rooftop units | 21% | 1820910 | 19600093.149 | 5.823% | 560 | 6 | 3360 | 36166.704 | 4.5208 | 305 | Gas | 555.3776 | 533.2922 | 5.555% | 228.806 | 823701.4925 | 5.177% | 11 | 397.8337 | 1358.6022 | 113.2169 | 0.7 | 25.3167 | 86.4565 | 7.2047 | 8.7196 | 315.36 | 1076.9544 | 89.7462 | 0% | 50% | 0% | 11 | 397.8337 | 1358.6022 | 113.2169 | 0.35 | 12.6583 | 43.2283 | 3.6024 | 8.7196 | 315.36 | 1076.9544 | 89.7462 | 3600 | 90
Class 'B' & 'C' - electric | 11% | 953810 | 10266715.459 | 3.05% | 560 | 6 | 3360 | 36166.704 | 4.5208 | 305 | Electric | 290.9121 | 279.3436 | 2.91% | 0 | 0 | 0% | 11 | 397.8337 | 1358.6022 | 113.2169 | 0.7 | 25.3167 | 86.4565 | 7.2047 | 8.7196 | 315.36 | 1076.9544 | 89.7462 | 0% | 50% | 0% | 11 | 397.8337 | 1358.6022 | 113.2169 | 0.35 | 12.6583 | 43.2283 | 3.6024 | 8.7196 | 315.36 | 1076.9544 | 89.7462 | 3600 | 0
RETAIL & HOSPITALITY | 100% | 5544000 | 59675061.6 | [6 empty] | N/A |  | 2669.1588 | 2720 | 28.33% | 1630 | 5868000 | 36.88%
Restaurant - gas MAU + RTU | 15% | 831600 | 8951259.24 | 2.66% | 140 | 1 | 140 | 1506.946 | 1 | 1500 | Gas | 1247.4 | 1271.16 | 13.24% | 277.8409 | 1000227.2727 | 6.286% | 82.5805 | 124.4444 | 424.9777 | 35.4148 | 34.9752 | 52.7058 | 179.9903 | 14.9992 | 53.4804 | 80.592 | 275.2217 | 22.9351 | 0% | 50% | 0% | 82.5805 | 124.4444 | 424.9777 | 35.4148 | 17.4876 | 26.3529 | 89.9952 | 7.4996 | 53.4804 | 80.592 | 275.2217 | 22.9351 | 3600 | 15
High-rise hotel - gas boiler | 13% | 720720 | 7757758.008 | 2.305% | 1100 | 20 | 22000 | 236805.8 | 438.5293 | 312 | Gas | 224.8646 | 229.1478 | 2.387% | 240.7955 | 866863.6364 | 5.448% | 9.2556 | 2191.79 | 7484.9628 | 623.7469 | 6.2 | 1468.196 | 5013.8892 | 417.8241 | 6 | 1420.8348 | 4852.1508 | 404.3459 | 0% | 50% | 0% | 9.2556 | 2191.79 | 7484.9628 | 623.7469 | 3.1 | 734.098 | 2506.9446 | 208.9121 | 6 | 1420.8348 | 4852.1508 | 404.3459 | 12000 | 0
High-rise hotel - electric | 12% | 665280 | 7161007.392 | 2.128% | 1100 | 20 | 22000 | 236805.8 | 438.5293 | 312 | Electric | 207.5674 | 211.521 | 2.203% | 0 | 0 | 0% | 9.2556 | 2191.79 | 7484.9628 | 623.7469 | 6.2 | 1468.196 | 5013.8892 | 417.8241 | 6 | 1420.8348 | 4852.1508 | 404.3459 | 0% | 50% | 0% | 9.2556 | 2191.79 | 7484.9628 | 623.7469 | 3.1 | 734.098 | 2506.9446 | 208.9121 | 6 | 1420.8348 | 4852.1508 | 404.3459 | 5000 | 0
Standalone retail | 25% | 1386000 | 14918765.4 | 4.433% | 140 | 1 | 140 | 1506.946 | 1 | 235 | Gas | 325.71 | 331.914 | 3.457% | 463.0682 | 1667045.4545 | 10.48% | 9 | 13.5625 | 46.316 | 3.8597 | 0.7 | 1.0549 | 3.6024 | 0.3002 | 11 | 16.5764 | 56.6084 | 4.7174 | 0% | 50% | 0% | 9 | 13.5625 | 46.316 | 3.8597 | 0.35 | 0.52743 | 1.8012 | 0.1501 | 11 | 16.5764 | 56.6084 | 4.7174 | 720 | 5
Mall retail | 35% | 1940400 | 20886271.56 | 6.206% | 10000 | 2 | 20000 | 215278 | 61.508 | 342 | Gas | 663.6168 | 676.2571 | 7.044% | 648.2955 | 2333863.6364 | 14.67% | 8 | 1722.224 | 5881.395 | 490.1162 | 0.7 | 150.6946 | 514.6221 | 42.8852 | 11 | 2368.058 | 8086.9181 | 673.9098 | 0% | 50% | 0% | 8 | 1722.224 | 5881.395 | 490.1162 | 0.35 | 75.3473 | 257.311 | 21.4426 | 11 | 2368.058 | 8086.9181 | 673.9098 | 0 | 0
MULTI-UNIT RESIDENTIAL | 100% | 10711000 | 115292132.9 | [6 empty] | N/A |  | 2506.374 | 2500 | 26.04% | 1300 | 4680000 | 29.41%
Pre-2004 apartment - gas boiler | 31% | 3320410 | 35740561.199 | 10.62% | 1850 | 12 | 22200 | 238958.58 | 238.9586 | 234 | Gas | 776.9759 | 775 | 8.073% | 419.7917 | 1511250 | 9.498% | 9 | 2150.6272 | 7344.392 | 612.0327 | 6.1704 | 1474.4769 | 5035.3386 | 419.6115 | 6 | 1433.7515 | 4896.2613 | 408.0218 | 0% | 50% | 0% | 9 | 2150.6272 | 7344.392 | 612.0327 | 3.0852 | 737.2384 | 2517.6693 | 209.8058 | 6 | 1433.7515 | 4896.2613 | 408.0218 | 12000 | 0
Pre-2004 apartment - electric | 4% | 428440 | 4611685.316 | 1.37% | 1850 | 12 | 22200 | 238958.58 | 238.9586 | 234 | Electric | 100.255 | 100 | 1.042% | 0 | 0 | 0% | 9 | 2150.6272 | 7344.392 | 612.0327 | 6.1704 | 1474.4769 | 5035.3386 | 419.6115 | 5.867 | 1401.9743 | 4787.7422 | 398.9785 | 0% | 50% | 0% | 9 | 2150.6272 | 7344.392 | 612.0327 | 3.0852 | 737.2384 | 2517.6693 | 209.8058 | 5.867 | 1401.9743 | 4787.7422 | 398.9785 | 12000 | 0
Post-2004 condo (window glazing alternate) |  |  |  |  | 750 | 30 | 22500 | 242187.75 | 306.5668
Post-2004 condo | 65% | 6962150 | 74939886.385 | 22.27% | 750 | 30 | 22500 | 242187.75 | 306.5668 | 234 | Gas | 1629.1431 | 1625 | 16.93% | 880.2083 | 3168750 | 19.91% | 9 | 2179.6898 | 7443.6405 | 620.3034 | 6.1704 | 1494.4023 | 5103.3837 | 425.282 | 5.5733 | 1349.7827 | 4609.5079 | 384.1257 | 0% | 50% | 0% | 9 | 2179.6898 | 7443.6405 | 620.3034 | 3.0852 | 747.2011 | 2551.6919 | 212.641 | 5.5733 | 1349.7827 | 4609.5079 | 384.1257 | 12000 | 0
RESIDENTIAL | 100% | 2848000 | 30655587.2 | [6 empty] | N/A |  | 712 | 510 | 5.312% | 360 | 1296000 | 8.145%
Typical house (Pitched Roof)(Int. Wall Reno) |  |  |  |  | 90 | 2.5 | 225 | 2421.8775 | 1.25
Typical house (Flat Roof)(Ext. Wall Reno) | 100% | 2848000 | 30655587.2 | 9.108% | 90 | 2.5 | 225 | 2421.8775 | 1.25 | 250 | Gas | 712 | 510 | 5.312% | 360 | 1296000 | 8.145% | 10 | 24.2188 | 82.7071 | 6.8923 | 9.6454 | 23.36 | 79.7744 | 6.6479 | 5.25 | 12.7149 | 43.4212 | 3.6184 | 0% | 50% | 0% | 10 | 24.2188 | 82.7071 | 6.8923 | 4.8227 | 11.68 | 39.8872 | 3.3239 | 5.25 | 12.7149 | 43.4212 | 3.6184 | 0 | 0
INSTITUTIONAL | 100% | 3495000 | 37619830.5 | [6 empty] | N/A |  | 1544.79 | 1540 | 16.04% | 400 | 1440000 | 9.05%
High water use hospital (inpatient) | 10% | 349500 | 3761983.05 | 1.118% | 4650 | 24 | 111600 | 1201251.24 |  | 782 | Gas | 273.309 | 272.4615 | 2.838% | 40 | 144000 | 0.905% | 16.333 | 19620 | 67002.3 | 5583.525 | 6.2 | 7447.7577 | 25434.0925 | 2119.5077 | 0 | 0 | 0 | 0 | 0% | 50% | 0% | 16.333 | 19620 | 67002.3 | 5583.525 | 3.1 | 3723.8788 | 12717.0463 | 1059.7539 | 0 | 0 | 0 | 0 | 0 | 0
Low water use hospital (outpatient) | 10% | 349500 | 3761983.05 | 1.118% | 3355 | 9 | 30195 | 325015.9605 |  | 254 | Gas | 88.773 | 88.4977 | 0.9219% | 40 | 144000 | 0.905% | 59.074 | 19200 | 65568 | 5464 | 6.2 | 2015.099 | 6881.5629 | 573.4636 | 0 | 0 | 0 | 0 | 0% | 50% | 0% | 59.074 | 19200 | 65568 | 5464 | 3.1 | 1007.5495 | 3440.7815 | 286.7318 | 0 | 0 | 0 | 0 | 0 | 0
Assembly & educational | 80% | 2796000 | 30095864.4 | 8.942% | 2500 | 3 | 7500 | 80729.25 |  | 423 | Gas | 1182.708 | 1179.0407 | 12.28% | 320 | 1152000 | 7.24% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 50% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL |  | 31269000 | 336576389.1 | 100% | [7 empty] | 9858.8154 | 9600 | 100% | 4420 | 15912000 | 100%
Note on N4: User Note: for context to the reference EUI values (use of updating), please use the following links https://natural-resources.canada.ca/energy-efficiency/energy-star-canada/energy-star-for-buildings/energy-benchmarking-technical-information/building-energy-use-surveys/19454 https://portfoliomanager.energystar.gov/pdf/reference/Canadian%20National%20Median%20Table.pdf
Note on Q4: User Note: The energy allocated to each subcategory, based on measured energy use per occupancy area, allocated based on sub-category size and energy use.
Note on C6: User Note: If this is dark green, then the percentages enetered are equal to 100%, but if it is red, please change the percentages to add up to 100%
Note on C13: User Note: If this is dark green, then the percentages enetered are equal to 100%, but if it is red, please change the percentages to add up to 100%
Note on C20: User Note: If this is dark green, then the percentages enetered are equal to 100%, but if it is red, please change the percentages to add up to 100%
Note on C26: User Note: If this is dark green, then the percentages enetered are equal to 100%, but if it is red, please change the percentages to add up to 100%
Note on C30: User Note: If this is dark green, then the percentages enetered are equal to 100%, but if it is red, please change the percentages to add up to 100%

## System Descriptions
Toronto 2030 District
Occupancy & Sub-Categories | BUILDING TYPOLOGIES |  |  |  | LIKE FOR LIKE RETROFIT (Base Case) |  | ASHP RETROFIT |  | ASHP w RNG BACKUP |  | GSHP RETROFIT |  | ELECTRIC RESISTANCE RETROFIT |  | HYDROGEN CONVERSION RETROFIT |  | Baseline Building Envelope |  |  | BAU Building Envelope Replacement |  |  | Option 1 Building Envelope Replacement
| Typology - Archetype Mechanical System Description | Hot Water Level (s, m ,l) | Ventilation Level (s, m ,l) | Stationary Engineer likely needed for heat pump? | Mechanical System End-of-Life Renewal Description | Electrical System Description | Mechanical System Conversion Description | Electrical System Description | Mechanical System Conversion Description | Electrical System Description | Mechanical System Conversion Description | Electrical System Description | Mechanical System Conversion Description | Electrical System Description | Mechanical System Conversion Description | Electrical System Description | Wall Description | Window Description | Roof Description | Replacement Wall Description | Replacement Window Description | Replacement Roof Description | Replacement Wall Description | Replacement Window Description | Replacement Roof Description | ERV Description | Upgrade and Replacement Recommendations
OFFICE
Class 'A' - gas boiler | rooftop gas boiler system ¦ 8,000MBH estimated boiler plant size ¦ (160F-180F)¦ 800MBH Water heating | low | medium | Yes | Assume boilers and water heating systems are replaced. | no significant electrical change | replace gas boiler with ashp, 3-4 large air-source, rooftop units required,(each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Upgrade electrical service: additional 400A capacity required, assume capacity is within existing TX capacity (~2MVA) Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Augment gas boiler backup plant with 2 large air-source, rooftop units (each 165 ton-223 tons). Add 75 ton polishing water to water heat pump to increase supply temperature to 160F, with RNG backup; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Use elec point-of-use domestic water heating with load-shifting control to minimize peak contribution; increase storage tank size to reduce required heat pump size. | Upgrade electrical service: additional 400A capacity required, assume capacity is within existing TX capacity (~2MVA) Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | replace gas boiler with GSHP, 3-4 large reversible chillers required (each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add geothermal sourced domestic hot water systems; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace gas boiler with electric resistance boiler, and electric DWH. | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | Assume boilers and water heating systems are replaced. | no significant electrical change | n/a | 20+ year old curtain wall (R2) | concrete, 2" eps (R3.5/"), waterproof membrane, gravel | n/a | replace double pane, sealed unit, low-e coating, not argon filled, not thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | n/a | Kawneer 2500UT or Flynn 9450 (Double Glazed, Thermally Broken Curtain Wall) | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide new, 85% efficient Energy Recovery Ventilator(s) exhausting all washrooms and common exhaust, and providing all OA for the building. Assume 1 main MUA. Assume 1x 29000 MUA and 2x 14,500CFM exhaust fans demolished to make room. | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 4 air source heat pump chiillers - control of 8 heating and cooling pumps - Control of main air handler - central monitoring of zone temperatures (per 5000ft2) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
Class 'A' - district heating/ cooling | hydronic hot water loop (160-180F design temp)¦ 8,000MBH estimated heat exchanger from DES ¦ (160F-180F) ¦ 800MBH Water heating also from DES | low | medium | Yes | Assume heat exchangers (8000MBH) and water heating heat exchange systems (800MBH) are replaced. | no significant electrical change | replace DES with ashp plant , 3-4 large air-source, rooftop units required,(each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Assume that DES buildings do not require removal of chiller and cooling tower. Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Upgrade electrical service: additional 400A capacity required, assume capacity is within existing TX capacity (2MVA) Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Augment gas boiler backup plant with 2 large air-source, rooftop units (each 165 ton-223 tons). Add 75 ton polishing water to water heat pump to increase supply temperature to 160F, with RNG backup; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Upgrade electrical service: additional 400A capacity required, assume capacity is within existing TX capacity (2MVA) Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | replace DES with GSHP, 3-4 large reversible chillers required (each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add geothermal sourced domestic hot water systems; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace DES with electric resistance boiler, and electric DWH. | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | Assume heat exchangers (8000MBH) and water heating heat exchange systems (800MBH) are replaced. | no significant electrical change | n/a | 20+ year old curtain wall (R2) | concrete, 2" eps (R3.5/"), waterproof membrane, gravel | n/a | replace double pane, sealed unit, low-e coating, not argon filled, not thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | n/a | Kawneer 2500UT or Flynn 9450 (Double Glazed, Thermally Broken Curtain Wall) | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide new, 85% efficient Energy Recovery Ventilator(s) exhausting all washrooms and common exhaust, and providing all OA for the building. Assume 1 main MUA. Assume 1x 29000 MUA and 2x 14,500CFM exhaust fans demolished to make room. | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 2 district energy cooling heat exchangers - ADD modulating main line steam control valve (4" dia) c/w new controls air compressor - Control of main air handler - control of 8 heating and cooling pumps - central monitoring of zone temperatures (per 5000ft2) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
Class 'A' - electric | Baseboard electric / 2,750 MBH fresh air MAUs (~30000CFM). Electric hot water heating. | low | medium | - | Assume make-up air unit is replaced; baseboard heaters are not replaced. | no significant electrical change | Replace MAUs with air-source cold climate heat pump sytle AHUs (80 tons total.) Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20%. Assume that heating load (kw) is higher than ASHP load (heating and cooling). Assume 2.6mw of existing electric heating. | Replace MAUs with air-source cold climate heat pump sytle AHUs (80 tons total.) Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20%. Assume that heating load (kw) is higher than ASHP load (heating and cooling). Assume 2.6mw of existing electric heating. | Replace MAUs with geo-source WSHP AHUs (80 tons total.) Add geothermal sourced domestic hot water systems; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace MAU with electric resistance MAUs (800KW total electric heating.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume make-up air unit is replaced; baseboard heaters are not replaced. | no significant electrical change | n/a | 20+ year old curtain wall (R2) | concrete, 2" eps (R3.5/"), waterproof membrane, gravel | n/a | replace double pane, sealed unit, low-e coating, not argon filled, not thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | n/a | Kawneer 2500UT or Flynn 9450 (Double Glazed, Thermally Broken Curtain Wall) | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide new, 85% efficient Energy Recovery Ventilator(s) exhausting all washrooms and common exhaust, and providing all OA for the building. Assume 1 main MUA. Assume 1x 29000 MUA and 2x 14,500CFM exhaust fans demolished to make room. | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 4 split DX - Control of 4 main air handlers and associated electric heating coils. - central monitoring of zone temperatures (per 5000ft2) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
Class 'B' & 'C' - rooftop units | Packaged gas-fired rooftop units; boiler-fed perimeter heating and rooftop gas burner with dx ¦ 1400 MBH total connected gas load, assume 6 x 15 ton RTUs +500MBH boiler | low | medium | - | Assume Packaged gas-fired rooftop units are replaced; boiler-fed perimeter heating and rooftop gas burner with dx ¦ 1700 MBH total connected gas load, assume 6 x 15 ton RTUs +500MBH boiler | no significant electrical change | Install new VRF heating system, with one new VRF heated, 3600CFM MUA (15 tons.) .Add VRF-coupled domestic hot water at each washroom, or use CO2 based high temperature system. | Assume service size is 400A, ASHP adds an additional 80-100kw of connected load. Service upgrade: new TX (500KVA), new main panel (600Amps). | Install new asir source heat pump RTUS, with one new VRF heated, 3600CFM MUA (15 tons.) Use electric resistance DWH | Assume service size is 400A, ASHP adds an additional 80-100kw of connected load. Service upgrade: new TX (500KVA), new main panel (600Amps). | Install new water-to-air heat pumps C/W, 3600CFM MUA (15 tons). Add geo-sourced DWH to serve washrooms. | replace RTU heating with rooftop glycol-to-air geothermal heat pumps, with new geothermal wells, cooling load = heating load, no change to electrical capacity, Electrical work required for switch over (labour), changes to breakers, feeder work, deisgn contigency | Install electric packaged RTUs, complete with six 65KW electric resistance heaters, and 146KW electric boiler, and new 30KW electric water heater (or more likely, 6x5KW water heaters, 1 / floor.) | assuming all electric with electric coil for ventilation air ¦ Six 65KW electric resistance heaters, adding duct heater load = 390kw additional load - cooling load (90tons=315kw) = 75kw additional load on service, replace main transformer (400kva to 500kva), replace main switchboard to 800A, feeder work, changes for breakers, design contingency | Assume Packaged gas-fired rooftop units are replaced; boiler-fed perimeter heating and rooftop gas burner with dx ¦ 1700 MBH total connected gas load, assume 6 x 15 ton RTUs +500MBH boiler | no significant electrical change | punch windows (find ratio), fibreglass batt insulated steel stud supporting 4" brick, plywood, waterproofing, brick ledge | double pane window, aluminum frame, no coatings | concrete, 2" eps, waterproof membrane, gravel | replace steel studs, put on 1/2" ply, thermal clips, 4" roxul, framed cladding system | Triple glazed, double low-E, argon filled, metal frames, thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | replace steel studs, put on 1/2" ply, thermal clips, 4" roxul, framed cladding system | Triple glazed, double low-E, argon filled, metal frames, thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide 6 new, 70% efficient bolt-on Energy Recovery Ventilators at each RTU. Re-duct washroom exhaust to nearest RTU. | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 6 x 15 ton rooftop units - central monitoring of zone temperatures (1 per 2500ft2)
Class 'B' & 'C' - electric | Baseboard electric / 600 MBH (3600CFM) rooftop gas-fired fresh air MAU (natural gas). Electric hot water heating. | low | medium | - | Assume make-up air unit is replaced; baseboard heaters are not replaced. | no significant electrical change | Install new VRF heated, 3600CFM MUA (15 tons) .Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20%. Assume that heating load (kw) is higher than ASHP load (heating and cooling). Assume 400KW of existing electric heating. | Install new VRF heated, 3600CFM MUA (15 tons) .Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20%. Assume that heating load (kw) is higher than ASHP load (heating and cooling). Assume 400KW of existing electric heating. | Install new geo WSHP serviced 3600CFM MUA (15 tons). Add geo-sourced DWH to serve washrooms. | replace RTU heating with rooftop glycol-to-air geothermal heat pumps, with new geothermal wells, cooling load = heating load, no change to electrical capacity, Electrical work required for switch over (labour), changes to breakers, feeder work, deisgn contigency | Install new electric MAU (175 KW heating required) and new 30KW electric water heater (or more likely, 6x5KW water heaters, 1 / floor.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume make-up air unit is replaced; baseboard heaters are not replaced. | no significant electrical change | punch windows (find ratio), fibreglass batt insulated steel stud supporting 4" brick, plywood, waterproofing, brick ledge | double pane window, aluminum frame, no coatings | concrete, 2" eps, waterproof membrane, gravel | 4” EIFS, add trowel on vapour barrier, EXPS, 2 coats acrylic stucco. . 4-6” metal composite panels, cw/ thermally broken clips. (Kingspan, non-combustible) | Triple glazed, double low-E, argon filled, metal frames, thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | 4” EIFS, add trowel on vapour barrier, EXPS, 2 coats acrylic stucco. . 4-6” metal composite panels, cw/ thermally broken clips. (Kingspan, non-combustible) | Triple glazed, double low-E, argon filled, metal frames, thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide 6 new, 70% efficient bolt-on Energy Recovery Ventilators at each RTU. Re-duct washroom exhaust to nearest RTU (assume 100' x 2'x3' ductwork) | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 6 x 15 ton rooftop units - central monitoring of zone temperatures (1 per 2500ft2)
RETAIL & HOSPITALITY
Restaurant - gas MAU + RTU | Gas make-up air heating providing dining area conditioning, with a 12' kitchen exhaust hood (3600CFM, 275MBH) and second gas-fired heating unit (150MBH) ¦ 425 MBH total connected gas load, excluding cooking equipment | high | high | - | Assume gas make-up air heating providing dining area conditioning and second gas-fired heating unit (150MBH) are replaced, as well as the water heatin system. | no significant electrical change | Assume VRF make-up air heating provides dining area conditioning (23 ton) and second gas-fired heating unit (12) are replaced with low-temperature compatible ASHP rooftop units. Add CO2 based water heating system (7 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume VRF make-up air heating provides dining area conditioning (23 ton) and second gas-fired heating unit (12) are replaced with low-temperature compatible ASHP rooftop units. Add CO2 based water heating system (7 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume MAU and RTU are replaced by geo WSHP make-up air heating provides dining area conditioning (23 ton) and second WSHP (12 tons) Add geo-sourced DWH to serve washrooms. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume gas make-up air heating providing dining area conditioning (80KW) and second gas-fired heating unit (44KW) are replaced with electric units, as well as the water heating system. | Replace incoming service from 400A to 800A | Assume gas make-up air heating providing dining area conditioning and second gas-fired heating unit (150MBH) are replaced, as well as the water heatin system. | no significant electrical change | 8" CMU Wall | Single plane storefront window | concrete, 2" eps, waterproof membrane, gravel | Add 4" EIFS to Concrete Block Wall | Double pane, thermally broken frame. E.g. (https://www.kawneer.com/kawneer/north_america/catalog/product_flyers/17-2287_TF601_601T_601UT.pdf) | replace 2" eps (R3.5/"), waterproof membrane, gravel | Add 4" EIFS to Concrete Block Wall | Double pane, thermally broken frame. E.g. (https://www.kawneer.com/kawneer/north_america/catalog/product_flyers/17-2287_TF601_601T_601UT.pdf) | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide new, 85% efficient Energy Recovery Ventilator(s) for washroom exhaust only. | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of one rooftop unit, - monitoring of kitchen MUA, and exhaust system. - central monitoring of zone temperatures (per 2500ft2)
High-rise hotel - gas boiler | 2 or 4 pipe hot water terminal units w/ 12,000 cfm gas-fired rooftop makeup air unit, 7500MBh total plant size with backup, central gas-fired hot water (85% ef, 5000MBH total installed, with backup.) | high | low | Yes | Assume boilers and water heating systems are replaced. | no significant electrical change | Complete system replacement with air source VRF system (650 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Assume no additional electrical load (cooling higher than new heating. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Complete system replacement with air source VRF system (650 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Assume no additional electrical load (cooling higher than new heating. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Complete system replacement with air source VRF system (650 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons) since geo will not balance for this occupancy type with DWH included. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume boilers (2190KW) and water heating systems (1470KW) are replaced with electric systems. | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | Assume boilers and water heating systems are replaced. | no significant electrical change | Pre-cast concrete panels, insulation between steel studs. | Double-glazed aluminum frame punched windows. | concrete deck, 2" eps (R3.5/"), waterproof membrane, gravel | Exterior applied EIFS panels (4") | Triple glazed, double low-E, argon filled, metal frames, thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | Exterior applied EIFS panels (4") | Triple glazed, double low-E, argon filled, metal frames, thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide one new 100cfrm ERV for each hotel room (170 suites). Assume 82% efficient ERV, BOD FV-10VEC1 | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of chiller and coolign tower - control of 4-boiler heating plant. - control of 8 heating and cooling pumps - Control of 2 corridor pressurization units - central monitoring and control of common area zone temperatures (30) - central monitoring and control of suite terminal units (smart networked thermostats.) (170) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
High-rise hotel - electric | Through-the-wall PTAC, 70% ASHP (standard type), 30% electric resistance. All operate as electric resistance on a design day. 600MBH (5000CFM) corridor pressurization MAU, 5000MBH DWH plant. | high | low | - | Through-the-wall PTAC, 70% ASHP (standard type), 30% electric resistance. All operate as electric resistance on a design day (170 rooms). MAU replaced with like. | no significant electrical change | New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20%. Assume that heating load (kw) is higher than ASHP load (heating and cooling). | New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20%. Assume that heating load (kw) is higher than ASHP load (heating and cooling). | New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) Add CO2 based water heating system (209 tons) since geo will not balance for this occupancy type with DWH included. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Through-the-wall PTAC, 70% ASHP (standard type), 30% electric resistance. All operate as electric resistance on a design day (170 rooms). MAU replaced with electric resistance type (175KW heating) | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | Through-the-wall PTAC, 70% ASHP (standard type), 30% electric resistance. All operate as electric resistance on a design day (170 rooms) | no significant electrical change | Pre-cast concrete panels, insulation between steel studs. | Double-glazed aluminum frame punched windows. | concrete deck, 2" eps (R3.5/"), waterproof membrane, gravel | Exterior applied EIFS panels (4") | Triple glazed, double low-E, argon filled, metal frames, thermally broken | replace 2" eps (R3.5/"), waterproof membrane, gravel | Exterior applied EIFS panels (4") | Triple glazed, double low-E, argon filled, metal frames, thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide one new 100cfrm ERV for each hotel room (170 suites). Assume 82% efficient ERV, MICRA 200 or equal (vents.ua) | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - Control of 2 corridor pressurization units - central monitoring and control of common area zone temperatures (30) - central monitoring and control of suite terminal units (smart networked thermostats.) (170)
Standalone retail | Packaged gas rooftop units, one 5-ton unit (150MBH) | low | medium | - | Packaged gas rooftop units, one 5-ton unit (150MBH) | no significant electrical change | Complete system replacement with air source VRF system (5 tons) and ERV for ventilation with 2KW electric preheat. Electric resistance water heating existing to remain. | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Complete system replacement with air source VRF system (5 tons) and ERV for ventilation with 2KW electric preheat. Electric resistance water heating existing to remain. | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Complete system replacement with air source VRF system (5 tons) and ERV for ventilation with 2KW electric preheat. Electric resistance water heating existing to remain. (Not a geo solution due to size of building) | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace one 5-ton rooftop unit with electric type (45KW heating.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Packaged gas rooftop units, one 5-ton unit (150MBH) | no significant electrical change | 8” CMU | Single pane storefront window | concrete deck, 2" eps (R3.5/"), waterproof membrane, gravel | Externally applied 4" EIFS | Double pane, thermally broken frame. E.g. (https://www.kawneer.com/kawneer/north_america/catalog/product_flyers/17-2287_TF601_601T_601UT.pdf) | replace 2" eps (R3.5/"), waterproof membrane, gravel | Externally applied 4" EIFS | Double pane, thermally broken frame. E.g. (https://www.kawneer.com/kawneer/north_america/catalog/product_flyers/17-2287_TF601_601T_601UT.pdf) | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide 1 new, 82% efficient bolt-on Energy Recovery Ventilator at the RTU. Re-duct washroom exhaust back to RTU (allow for running over dropped ceiling ~60'.) | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of one 15 ton rooftop unit - central monitoring of zone temperatures (1 per 2500ft2)
Mall retail | 6,000MBH boiler plant serving perimeter heating and fresh air (typically, retail unit terminal systems are heating only.) ¦ 160-180F | low | medium | Yes | Replace 6,000MBH boiler plant. | no significant electrical change | replace gas boiler with ashp, 3-4 large air-source, rooftop units required,(each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Augment gas boiler backup plant with 2 large air-source, rooftop units (each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add CO2 based domestic water heating heat pumps; increase storage tank size to reduce required heat pump size. | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace gas boiler with GSHP, 3-4 large water-source WSHPs (each 165 ton-223 tons). Add 150 ton polishing water to water heat pump to increase supply temperature to 160F; retrofit system to provide cascade heating loop to permit lower temperature return water. Remove existing cooling tower and chillers. Add geo-sourced DWH to serve washrooms. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace 6,000MBH boiler plant with 1756KW electric boilers, plus, 150KW domestic potable water heaters. | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | 4,000MBH boiler plant serving perimeter heating and fresh air (typically, retail unit terminal systems are heating only.) ¦ 160-180F | no significant electrical change | no info | no info | no info | no info | no info | no info | no info | no info | no info | TBD - appropriate, but we should ask mall owners to comment on cost & prototype. Not possible to predict on a generalized basis. | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 4 air source heat pump chiillers - control of 8 heating and cooling pumps - Control of main air handler - central monitoring of zone temperatures (per 4000ft2) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
MULTI-UNIT RESIDENTIAL
Pre-2004 apartment - gas boiler | 2 or 4 pipe hot water terminal units w/ 12,000 cfm gas-fired rooftop makeup air unit, 7500MBh total plant size with backup, central gas-fired hot water (85% ef, 5000MBH total installed, with backup.) | high | low | - | Assume gas boilers and hot water heating boilers are replaced. | no significant electrical change | Complete system replacement with air source VRF system (610 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Complete system replacement with air source VRF system (610 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Electrically, assume new 600 ton retrofit GSHP has been provided. Detailed assumptions for heat pump / 2-pipe /4pipe are below the main table. Add CO2 based water heating system (209 tons) since geo will not balance for this occupancy type with DWH included. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume gas boilers (2170KW capacity), hot water heating boilers (1470KW capacity) are replaced. | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | Assume gas boilers, hot water heating boilers and MAU are replaced. | no significant electrical change | 4” brick, 25mm air space, 3-5/8” LWSS w/ fibreglass insulation, VB, 5/8” drywall | Double-glazed aluminum frame punched windows. | concrete deck, 2" eps (R3.5/"), waterproof membrane, gravel | replace 3-5/8” LWSS w/ fibreglass insulation, VB, 5/8” drywall | replace Double-glazed aluminum frame punched windows, not thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | 4” EIFS, add trowel on vapour barrier, EXPS, 2 coats acrylic stucco. . 4-6” metal composite panels, cw/ thermally broken clips. (Kingspan, non-combustible) | Triple glazed, double low-E, argon filled, metal frames, thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide one new 100cfrm ERV for each suite (237 suites). Assume 82% efficient ERV, BOD FV-10VEC1 | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 4 air source heat pump chiillers - control of 8 heating and cooling pumps - Control of main air handler - central monitoring and control of common area zone temperatures (10) - central monitoring and control of suite terminal units (smart networked thermostats.) (237 count) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
Pre-2004 apartment - electric | Electric Resistance baseboards w/ gas-fired rooftop makeup air unit; central gas-fired hot water (85% ef). MAU assumed to be 12,000CFM and gas-fired. | high | low | - | Assume make-up air unit is replaced; baseboard heaters / electrical heating system is not replaced. DHW gas heaters replaced. | no significant electrical change | New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | New VRF MAU (100 tons.) Add CO2 based water heating system (209 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | New water-to-air MAU (100 tons.)Add CO2 based water heating system (209 tons) since geo will not balance for this occupancy type with DWH included. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | MAU replaced with electric resistance type (175KW heating), hot water heating boilers (1470KW capacity) are replaced. | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume make-up air unit is replaced; baseboard heaters / electrical heating system is not replaced. |  | 4” brick, 25mm air space, 3-5/8” LWSS w/ fibreglass insulation, VB, 5/8” drywall | Double-glazed aluminum frame punched windows. | concrete deck, 2" eps (R3.5/"), waterproof membrane, gravel | replace 3-5/8” LWSS w/ fibreglass insulation, VB, 5/8” drywall | replace Double-glazed aluminum frame punched windows, not thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | 4” EIFS, add trowel on vapour barrier, EXPS, 2 coats acrylic stucco. . 4-6” metal composite panels, cw/ thermally broken clips. (Kingspan, non-combustible) | Triple glazed, double low-E, argon filled, metal frames, thermally broken | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide one new 100cfrm ERV for each suite (237 suites). Assume 82% efficient ERV, BOD Panasonic FV-10VEC1 | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - Control of 2 corridor pressurization units - central monitoring and control of common area zone temperatures (30) - central monitoring and control of suite terminal units (smart networked thermostats.) (237 count))
Post-2004 condo (window glazing alternate) | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | Double-glazed aluminum frame, window wall | no info | no info | Triple glazed, double low-E, argon filled, metal frames, thermally broken | no info | no info | Triple glazed, double low-E, argon filled, metal frames, thermally broken | no info | no info | no info
Post-2004 condo | 2 or 4 pipe hot water terminal units w/ 12,000 cfm gas-fired rooftop makeup air unit, 7500MBh total plant size, 92% eff with backup, central gas-fired hot water (92% ef, 5000MBH total installed, with backup.) | high | low | - | 2 or 4 pipe fancoil or in-suite heat pumps, gas fired boiler central plant, gas-fired rooftop makeup air unit; central gas-fired hot water (90%ef) | no significant electrical change | Complete system replacement with air source VRF system (620 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (212 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Complete system replacement with air source VRF system (620 tons). New VRF MAU (100 tons.) Add CO2 based water heating system (212 tons.) | Assume capacity is within existing TX capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Electrically, assume new 600 ton retrofit GSHP has been provided. Detailed assumptions for heat pump / 2-pipe /4pipe are below the main table. Add CO2 based water heating system (209 tons) since geo will not balance for this occupancy type with DWH included. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Assume gas boilers (2180KW capacity), hot water heating boilers (1490KW capacity) are replaced. | new HV transformer - 2.5mVA, New HV Switch, New 600V Switchboard - 3000A, New Feeder breakers - 4@600A, New 600V Feeders @$150/ft, assume 100ft/feeder, Misc (HV feeder, controls, etc), Design contingency 20% | 2 or 4 pipe fancoil or in-suite heat pumps, gas fired boiler central plant, gas-fired rooftop makeup air unit; central gas-fired hot water (90%ef) | no significant electrical change | Spandrel Panel | Double-glazed aluminum frame, window wall | concrete deck, 2" eps (R3.5/"), waterproof membrane, gravel | replace with thermally broken, highly insulated spandrel panel: e.g. https://lenmak.com/spandreltherm/ | Double glazed w/ mylar unit. | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | replace with thermally broken, highly insulated spandrel panel: e.g. https://lenmak.com/spandreltherm/ | Double glazed w/ mylar unit. | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide one new 100cfrm ERV for each suite (307 suites). Assume 82% efficient ERV, BOD Panasonic FV-10VEC1 | UPGRADE or REPLACE building automation system to include: - peak-shaving/demand response capability - weather forecast integrated to pre-heat building when cold weather is arriving. - control of 4 air source heat pump chiillers - control of 8 heating and cooling pumps - Control of main air handler - central monitoring and control of common area zone temperatures (10) - central monitoring and control of suite terminal units (smart networked thermostats.) (307 count) - ADD modulating zoning valves, assume 2" line size. (assume 1 / 10,000ft2)
RESIDENTIAL
Typical house (Pitched Roof)(Int. Wall Reno) | no info | no info | no info | - | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | 8” brick, 1.5” wood lathe, horsehair plaster |  | gypsum, rafters, 6" rigid ins. roof deck, plywood, vapor barrier, shingles. | add 2” eps, drywall |  | fill rafters with 18" insulation | add 2” eps, drywall | no info | fill rafters with 18" insulation | no info | no info
Typical house (Flat Roof)(Ext. Wall Reno) | Forced-air gas-fired furnace, 85% eff, 80MBH. Gas-fired DWH, also 80MBH. About 70% have central A/C. | high | low | - | Forced-air gas-fired furnace, 85% eff. About 70% have central A/C | no significant electrical change | New 5-ton cold-climate heat pump based furnace. Add CO2 based domestic hot water system. | Assume capacity is within existing Service capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | New 5-ton cold-climate heat pump based furnace. Add CO2 based domestic hot water system. | Assume capacity is within existing Service capacity. Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | New 5-ton heat pump based furnace with desuperheater and additional capacity for DWH heating. 3KW electric DWH polishing coil and tank. | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace home heating with with 20KW electric furnace. Replace water heater with electric heater with higher storage capacity ( 9KW). Upgrade service to 200A. | Upgrage service to 400A | Forced-air gas-fired furnace, 85% eff. About 70% have central A/C | no info | 8” brick, 1.5” wood lathe, horsehair plaster | Wood frame double pane, low e, argon | gypsum, rafters, 6" rigid ins. roof deck, plywood, vapor barrier, shingles. | 5” Roxul, thermal clips, wood furring, metal panels | double-glazed vinyl window, low e argon. | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | 5” Roxul, thermal clips, wood furring, metal panels | Insulated fibreglass, triple pane. | 8" poly-iso, (R3.5 outer 2", and 5.6 for the rest)new membrane | Provide new 78% efficient Energy Recovery Ventilator for furnace. ( Basis of Design: RenewAireEV200) | This product is not currently available for the residential market, but I would expect the funcitonality required can be included in a smart thermostat (nest equal) at no additional cost over current market rate. Recommend also including a budget for a similar wireless IOT controller for the domestic water heater.
INSTITUTIONAL
High water use hospital (inpatient) | 5 Steam Boilers (19600 kw) | high | high | Yes | 5 Steam Boilers (19600 kw) | no info | no info | no info | no info | no info | no info | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace boilers with electric boilers | New HV switchgear sections. Potential new serice requried by Hydro | 5 Steam Boilers (19600 kw) | no info
Low water use hospital (outpatient) | 2 Steam Boilers and 2 Glycol Boilers (19169 kw) | low | medium | Yes | 2 Steam Boilers and 2 Glycol Boilers (19169 kw) | no info | no info | no info | no info | no info | no info | Electrical work required for switch over (labour), Changes to breakers, Feeder rework, Design Contingency 20% | Replace boilers with electric boilers | New HV switchgear sections. Potential new serice requried by Hydro | 2 Steam Boilers and 2 Glycol Boilers (19169 kw) | no info
Assembly & educational | no info | low | high | Yes | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info | no info
Note on A3: User Note: The contingency applied to each retrofit varied based on the quaility of information

## FS - Unitary Capital
Toronto 2030 District
Occupancy & Sub-Categories | LIKE FOR LIKE RETROFIT (Base Case) | [6 empty] | ASHP RETROFIT | [7 empty] | ASHP w RNG BACKUP | [9 empty] | GSHP RETROFIT | [9 empty] | ELECTRIC RESISTANCE RETROFIT | [6 empty] | HYDROGEN CONVERSION RETROFIT
| Unitary Cost - Space Heating | Unitary Cost - Water Heating | Unitary Cost - MAU Replacement | Unitary Cost - RTU Replacement | Unitary Cost - Space Cooling | Other Equipment | Electrical Capital Cost | Retrofit ASHP Size | Archetype DWH Heating Plant Size | Unitary Cost - Space Heating | Unitary Cost - Water Heating | Unitary Cost - MAU Replacement | Unitary Cost - RTU Replacement | Other Equipment | Electrical Capital Cost | ASHP % HP-fuelled | DHW % HP-fuelled | Retrofit ASHP Size | Archetype DWH Heating Plant Size | Unitary Cost - Space Heating | Unitary Cost - Water Heating | Unitary Cost - MAU Replacement | Unitary Cost - RTU Replacement | Other Equipment | Electrical Capital Cost | GSHP % HP-fuelled | DHW % HP-fuelled | Retrofit GSHP Size | Archetype DWH Heating Plant Size | Unitary Cost - Space Heating | Unitary Cost - Water Heating | Unitary Cost - MAU Replacement | Unitary Cost - RTU Replacement | Unitary Cost - Geothermal System | Electrical Capital Cost | Unitary Cost - Space Heating | Unitary Cost - Water Heating | Unitary Cost - MAU Replacement | Unitary Cost - RTU Replacement | Unitary Cost - Space Cooling | Other Equipment | Electrical Capital Cost | Unitary Cost - Space Heating | Unitary Cost - Water Heating | Unitary Cost - MAU Replacement | Unitary Cost - RTU Replacement | Unitary Cost - Space Cooling | Other Equipment | Electrical Capital Cost
Units | $/MBH | $/MBH | $/CFM | $/Ton | $/Ton | $ | $ | Tons | Tons Refrig | $/Ton | $/Ton | $/CFM | $/Ton | $/Building | $/Building | % | % | Tons | Tons Refrig | $/Ton | $/Ton | $/CFM | $/Ton | $/Building | $/Building | % | % | Tons | Tons Refrig | $/Ton | $/Ton | $/CFM | $/Ton | $/Ton | $/Building | $/MBH | $/MBH | $/CFM | $/Ton | $/Ton | $/Building | $/Building | $/MBH | $/MBH | $/CFM | $/Ton | $/Ton | $/Building | $/Building
OFFICE
Class 'A' - gas boiler | 57.5 | 105.8897 | 0 | 0 | 3000 | 0 | 0 | 771.9331 | 30.9948 | 7000 | 11200 | 0 | 0 | 1200000 | 750000 | 56% | 200% | 432.2825 | 61.9896 | 7000 | 689.7931 | 0 | 0 | 770000 | 750000 | 100% | 100% | 771.9331 | 30.9948 | 7500 | 6300 | 0 | 0 | 3300 | 300000 | 29.2826 | 58.5652 | 0 | 0 | 3000 | 0 | 1500000 | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0
Class 'A' - district heating/ cooling | 24.615 | 140.9743 | 0 | 0 | 240 | 0 | 0 | 771.9331 | 30.9948 | 7000 | 11200 | 0 | 0 | 840000 | 750000 | 56% | 200% | 432.2825 | 61.9896 | 7000 | 689.7931 | 0 | 0 | 539000 | 750000 | 100% | 100% | 771.9331 | 30.9948 | 7500 | 6300 | 0 | 0 | 3300 | 300000 | 29.2826 | 58.5652 | 0 | 0 | 240 | 0 | 1500000 | 20 | 20 | 0 | 0 | 240 | 0
Class 'A' - electric | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 771.9331 | 30.9948 | 0 | 11200 | 20 | 0 | 0 | 250000 | 56% | 200% | 432.2825 | 61.9896 | 0 | 0 | 20 | 0 | 0 | 250000 | 100% | 100% | 771.9331 | 30.9948 | 0 | 6300 | 15 | 0 | 3300 | 125000 | 0 | 0 | 15 | 0 | 0 | 0 | 400000 | 0 | 0 | 15 | 0 | 0 | 0
Class 'B' & 'C' - rooftop units | 21.1615 | 0 | 0 | 2200 | 0 | 0 | 0 | 113.2169 | 3.6019 | 8000 | 2221.0227 | 20 | 0 | 0 | 400000 | 100% | 50% | 113.2169 | 1.801 | 0 | 3331.534 | 20 | 5500 | 0 | 400000 | 100% | 100% | 113.2169 | 3.6019 | 7200 | 6300 | 15 | 0 | 3300 | 50000 | 33.1223 | 58.5652 | 0 | 2200 | 0 | 0 | 500000 | 42.3229 | 0 | 0 | 2200 | 0 | 0 | 0
Class 'B' & 'C' - electric | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 113.2169 | 3.6019 | 0 | 2221.0227 | 20 | 0 | 0 | 150000 | 56% | 50% | 63.4014 | 1.801 | 0 | 3331.534 | 20 | 0 | 0 | 150000 | 100% | 100% | 113.2169 | 3.6019 | 0 | 6300 | 15 | 0 | 3300 | 50000 | 0 | 58.5652 | 15 | 0 | 0 | 0 | 75000 | 0 | 0 | 15 | 0 | 0 | 0 | 0
RETAIL & HOSPITALITY
Restaurant - gas MAU + RTU | 0 | 131.1171 | 15 | 2200 | 0 | 0 | 0 | 35.4148 | 7.4987 | 0 | 11200 | 25 | 12320 | 0 | 100000 | 56% | 50% | 19.8323 | 3.7494 | 0 | 11200 | 25 | 12320 | 0 | 100000 | 100% | 100% | 35.4148 | 7.4987 | 0 | 6300 | 15 | 22050 | 3300 | 50000 | 0 | 58.5652 | 15 | 2200 | 0 | 0 | 350000 | 0 | 20 | 15 | 2200 | 0 | 0 | 0
High-rise hotel - gas boiler | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0 | 623.7469 | 208.8883 | 8000 | 8750 | 20 | 0 | 0 | 1250000 | 56% | 50% | 349.2983 | 104.4441 | 8000 | 8750 | 20 | 0 | 0 | 1250000 | 100% | 100% | 623.7469 | 208.8883 | 8000 | 8750 | 20 | 0 | 3300 | 1000000 | 29.2826 | 29.2826 | 0 | 0 | 3000 | 0 | 1500000 | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0
High-rise hotel - electric | 0 | 0 | 15 | 0 | 0 | 382500 | 0 | 623.7469 | 208.8883 | 0 | 8750 | 24 | 0 | 0 | 200000 | 56% | 50% | 349.2983 | 104.4441 | 0 | 8750 | 24 | 0 | 0 | 200000 | 100% | 100% | 623.7469 | 208.8883 | 0 | 8750 | 24 | 0 | 3300 | 150000 | 0 | 0 | 15 | 0 | 0 | 382500 | 400000 | 0 | 0 | 0 | 0 | 0 | 382500 | 0
Standalone retail | 0 | 0 | 0 | 2200 | 0 | 0 | 0 | 4.7174 | 0.15008 | 14000 | 0 | 20 | 0 | 0 | 40000 | 56% | 50% | 2.6417 | 0.075041 | 14000 | 0 | 20 | 0 | 0 | 40000 | 100% | 100% | 4.7174 | 0.15008 | 14000 | 0 | 20 | 0 | 3300 | 40000 | 0 | 0 | 0 | 2200 | 0 | 0 | 40000 | 0 | 0 | 0 | 2200 | 0 | 0 | 0
Mall retail | 57.5 | 96.3635 | 0 | 0 | 3000 | 0 | 0 | 673.9098 | 21.4401 | 7000 | 11200 | 0 | 0 | 1200000 | 750000 | 56% | 50% | 377.3895 | 10.7201 | 7000 | 11200 | 0 | 0 | 770000 | 750000 | 100% | 100% | 673.9098 | 21.4401 | 7000 | 11200 | 0 | 0 | 3300 | 750000 | 29.2826 | 58.5652 | 0 | 0 | 3000 | 0 | 1500000 | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0
MULTI-UNIT RESIDENTIAL
Pre-2004 apartment - gas boiler | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0 | 612.0327 | 209.7819 | 8000 | 8750 | 20 | 0 | 0 | 1250000 | 56% | 50% | 342.7383 | 104.8909 | 8000 | 8750 | 20 | 0 | 0 | 1250000 | 100% | 100% | 612.0327 | 209.7819 | 4872.2073 | 8750 | 7 | 0 | 3300 | 300000 | 29.2826 | 29.2826 | 0 | 0 | 3000 | 0 | 1500000 | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0
Pre-2004 apartment - electric | 0 | 57.5 | 15 | 0 | 3000 | 0 | 0 | 612.0327 | 209.7819 | 0 | 8750 | 10 | 0 | 0 | 250000 | 56% | 50% | 342.7383 | 104.8909 | 0 | 8750 | 10 | 0 | 0 | 250000 | 100% | 100% | 612.0327 | 209.7819 | 0 | 8750 | 7.5 | 0 | 3300 | 300000 | 0 | 29.2826 | 15 | 0 | 3000 | 0 | 400000 | 0 | 0 | 0 | 0 | 3000 | 0 | 0
Post-2004 condo (window glazing alternate)
Post-2004 condo | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0 | 620.3034 | 212.6168 | 8000 | 8750 | 20 | 0 | 0 | 1250000 | 56% | 50% | 347.3699 | 106.3084 | 8000 | 8750 | 20 | 0 | 0 | 1250000 | 100% | 100% | 620.3034 | 212.6168 | 4594.0424 | 8750 | 8 | 0 | 3300 | 300000 | 29.2826 | 29.2826 | 0 | 0 | 3000 | 0 | 1500000 | 57.5 | 57.5 | 0 | 0 | 3000 | 0 | 0
RESIDENTIAL
Typical house (Pitched Roof)(Int. Wall Reno)
Typical house (Flat Roof)(Ext. Wall Reno) | 253.908 | 62.6767 | 0 | 0 | 2708.3522 | 0 | 0 | 6.8923 | 3.3236 | 1741.0835 | 3008.8264 | 0 | 0 | 0 | 10000 | 100% | 50% | 6.8923 | 1.6618 | 1741.0835 | 6017.6528 | 0 | 0 | 0 | 10000 | 100% | 100% | 6.8923 | 3.3236 | 870.5418 | 752.2066 | 0 | 0 | 3300 | 10000 | 58.5652 | 30.0848 | 0 | 0 | 2708.3522 | 2400 | 25000 | 253.908 | 62.6767 | 0 | 0 | 2708.3522 | 0 | 0
INSTITUTIONAL
High water use hospital (inpatient) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5583.525 | 1059.6332 | 7000 | 8750 | 0 | 0 | 1200000 | 0 | 56% | 50% | 3126.774 | 529.8166 | 7000 | 8750 | 0 | 0 | 1200000 | 0 | 100% | 100% | 5583.525 | 1059.6332 | 7000 | 8750 | 0 | 0 | 3300 | 84000 | 29.2826 | 29.2826 | 0 | 0 | 0 | 0 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Low water use hospital (outpatient) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5464 | 286.6992 | 7000 | 8750 | 0 | 0 | 1200000 | 0 | 56% | 50% | 3059.84 | 143.3496 | 7000 | 8750 | 0 | 0 | 1200000 | 0 | 100% | 100% | 5464 | 286.6992 | 7000 | 8750 | 0 | 0 | 3300 | 84000 | 29.2826 | 29.2826 | 0 | 0 | 0 | 0 | 30000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly & educational | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on A3: User Note: The contingency applied to each retrofit varied based on the quaility of information
Note on C3: User Note: If there is no space heating plant, water heating plant, MAU, and etc. Just put input the unitary cost as $0
Note on K3: User Note: If there is no space heating plant, water heating plant, MAU, and etc. Just put input the unitary cost as $0
Note on T3: User Note: If there is no space heating plant, water heating plant, MAU, and etc. Just put input the unitary cost as $0
Note on AE3: User Note: If there is no space heating plant, water heating plant, MAU, and etc. Just put input the unitary cost as $0
Note on AP3: User Note: If there is no space heating plant, water heating plant, MAU, and etc. Just put input the unitary cost as $0
Note on AX3: User Note: If there is no space heating plant, water heating plant, MAU, and etc. Just put input the unitary cost as $0
Note on T4: User Note: This column is unique to this retrofit type - a hybrid plant is envisioned. This input represents the size of the dominant heating source of the hybrid system as a fraction of the total system size. The backup system is assumed to be sized for the full system size.
Note on AE4: User Note: This column is unique to this retrofit type - a hybrid plant is envisioned. This input represents the size of the dominant heating source of the hybrid system as a fraction of the total system size. The backup system is assumed to be sized for the full system size.
Note on H16: User Note: This is the cost for electric baseboard heater replacements - $1500/ unit
Note on A23: User Note: This row is not used in this tab - no formulas are included in this row
Note on A27: User Note: This row is not used in this tab - no formulas are included in this row

## FS - Capital Output
Toronto 2030 District
Occupancy & Sub-Categories | LIKE FOR LIKE RETROFIT (Base Case) | [8 empty] | ASHP RETROFIT | [7 empty] | ASHP w RNG BACKUP | [7 empty] | GSHP RETROFIT | [7 empty] | ELECTRIC RESISTANCE RETROFIT | [8 empty] | HYDROGEN CONVERSION RETROFIT
| Space Heating Plant Replacement | Water Heating Plant Replacement | MAU Replacement | RTU Replacement | Space Cooling Plant Replacement | Other Equipment | Electrical Capital Cost | Material and Labour Subtotal | Total (Including M&L, Tax, PM, GC, …) | Space Heating Plant Replacement | Water Heating Plant Replacement | MAU Replacement | RTU Replacement | Other Equipment | Electrical Capital Cost | Material and Labour Subtotal | Total (Including M&L, Tax, PM, GC, …) | Space Heating Plant Replacement | Water Heating Plant Replacement | MAU Replacement | RTU Replacement | Other Equipment | Electrical Capital Cost | Material and Labour Subtotal | Total (Including M&L, Tax, PM, GC, …) | Space Heating Plant Replacement | Water Heating Plant Replacement | MAU Replacement | RTU Replacement | Geothermal Field | Electrical Capital Cost | Material and Labour Subtotal | Total (Including M&L, Tax, PM, GC, …) | Space Heating Plant Replacement | Water Heating Plant Replacement | MAU Replacement | RTU Replacement | Space Cooling Plant Replacement | Other Equipment | Electrical Capital Cost | Material and Labour Subtotal | Total (Including M&L, Tax, PM, GC, …) | Space Heating Plant Replacement | Water Heating Plant Replacement | MAU Replacement | RTU Replacement | Space Cooling Plant Replacement | Other Equipment | Electrical Capital Cost | Material and Labour Subtotal | Total (Including M&L, Tax, PM, GC, …)
Units | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $
OFFICE
Class 'A' - gas boiler | 473452.2943 | 78777.6963 | 0 | 0 | 2315799.2655 | 0 | 0 | 2868029.2561 | 4699265.9361 | 5403531.6195 | 347141.7835 | 0 | 0 | 1200000 | 750000 | 7700673.403 | 12617553.3708 | 3025977.7069 | 42760 | 0 | 0 | 770000 | 750000 | 4588737.7069 | 7518646.7328 | 5789498.1638 | 195267.2532 | 0 | 0 | 2547379.1921 | 300000 | 8832144.609 | 14471468.9419 | 241111.36 | 21785.064 | 0 | 0 | 2315799.2655 | 0 | 1500000 | 4078695.6895 | 6682942.8872 | 473452.2943 | 21388.8481 | 0 | 0 | 2315799.2655 | 0 | 0 | 2810640.4079 | 4605234.3084
Class 'A' - district heating/ cooling | 202679.0589 | 104879.1987 | 0 | 0 | 185263.9412 | 0 | 0 | 492822.1988 | 807489.1728 | 5403531.6195 | 347141.7835 | 0 | 0 | 840000 | 750000 | 7340673.403 | 12027693.3708 | 3025977.7069 | 42760 | 0 | 0 | 539000 | 750000 | 4357737.7069 | 7140153.2328 | 5789498.1638 | 195267.2532 | 0 | 0 | 2547379.1921 | 300000 | 8832144.609 | 14471468.9419 | 241111.36 | 21785.064 | 0 | 0 | 185263.9412 | 0 | 1500000 | 1948160.3652 | 3192060.7584 | 164679.0589 | 7439.5994 | 0 | 0 | 185263.9412 | 0 | 0 | 357382.5995 | 585571.3892
Class 'A' - electric | 0 | 0 | 450000 | 0 | 0 | 0 | 0 | 450000 | 737325 | 0 | 347141.7835 | 600000 | 0 | 0 | 250000 | 1197141.7835 | 1961516.8123 | 0 | 0 | 600000 | 0 | 0 | 250000 | 850000 | 1392725 | 0 | 195267.2532 | 450000 | 0 | 2547379.1921 | 125000 | 3317646.4453 | 5435963.7006 | 0 | 0 | 450000 | 0 | 0 | 0 | 400000 | 850000 | 1392725 | 0 | 0 | 450000 | 0 | 0 | 0 | 0 | 450000 | 737325
Class 'B' & 'C' - rooftop units | 28750 | 0 | 0 | 198000 | 0 | 0 | 0 | 226750 | 371529.875 | 905734.8238 | 8000 | 72000 | 0 | 0 | 400000 | 1385734.8238 | 2270526.5089 | 0 | 6000 | 72000 | 495000 | 0 | 400000 | 973000 | 1594260.5 | 815161.3415 | 22692.2494 | 54000 | 0 | 373615.6148 | 50000 | 1315469.2057 | 2155396.2936 | 45000 | 2531.6693 | 0 | 198000 | 0 | 0 | 500000 | 745531.6693 | 1221553.6401 | 57500 | 0 | 0 | 198000 | 0 | 0 | 0 | 255500 | 418636.75
Class 'B' & 'C' - electric | 0 | 0 | 54000 | 0 | 0 | 0 | 0 | 54000 | 88479 | 0 | 8000 | 72000 | 0 | 0 | 150000 | 230000 | 376855 | 0 | 6000 | 72000 | 0 | 0 | 150000 | 228000 | 373578 | 0 | 22692.2494 | 54000 | 0 | 373615.6148 | 50000 | 500307.8643 | 819754.4356 | 0 | 2531.6693 | 54000 | 0 | 0 | 0 | 75000 | 131531.6693 | 215514.6401 | 0 | 0 | 54000 | 0 | 0 | 0 | 0 | 54000 | 88479
RETAIL & HOSPITALITY
Restaurant - gas MAU + RTU | 0 | 23599.8061 | 54000 | 33000 | 0 | 0 | 0 | 110599.8061 | 181217.7824 | 0 | 83985.9154 | 90000 | 184800 | 0 | 100000 | 458785.9154 | 751720.7223 | 0 | 41992.9577 | 90000 | 184800 | 0 | 100000 | 416792.9577 | 682915.2612 | 0 | 47242.0774 | 54000 | 330750 | 116868.8659 | 50000 | 598860.9433 | 981233.6556 | 0 | 5270.58 | 54000 | 33000 | 0 | 0 | 350000 | 442270.58 | 724660.3453 | 0 | 1799.9031 | 54000 | 33000 | 0 | 0 | 0 | 88799.9031 | 145498.6412
High-rise hotel - gas boiler | 430385.3591 | 288298.6292 | 0 | 0 | 1213037.7105 | 0 | 0 | 1931721.6988 | 3165126.0035 | 4989975.1778 | 1827772.359 | 240000 | 0 | 0 | 1250000 | 8307747.5368 | 13612244.3391 | 2794386.0996 | 913886.1795 | 240000 | 0 | 0 | 1250000 | 5198272.2791 | 8517369.1293 | 4989975.1778 | 1827772.359 | 240000 | 0 | 2058364.7608 | 1000000 | 10116112.2977 | 16575249.9997 | 219178.9976 | 73409.798 | 0 | 0 | 1213037.7105 | 0 | 1500000 | 3005626.5061 | 4924719.0302 | 430385.3591 | 144149.3146 | 0 | 0 | 1213037.7105 | 0 | 0 | 1787572.3842 | 2928937.3515
High-rise hotel - electric | 0 | 0 | 75000 | 0 | 0 | 382500 | 0 | 457500 | 749613.75 | 0 | 1827772.359 | 120000 | 0 | 0 | 200000 | 2147772.359 | 3519125.0102 | 0 | 913886.1795 | 120000 | 0 | 0 | 200000 | 1233886.1795 | 2021722.5051 | 0 | 1827772.359 | 120000 | 0 | 2058364.7608 | 150000 | 4156137.1199 | 6809830.6709 | 0 | 0 | 75000 | 0 | 0 | 382500 | 400000 | 857500 | 1405013.75 | 0 | 0 | 0 | 0 | 0 | 382500 | 0 | 382500 | 626726.25
Standalone retail | 0 | 0 | 0 | 11000 | 0 | 0 | 0 | 11000 | 18023.5 | 66043.1642 | 0 | 14400 | 0 | 0 | 40000 | 120443.1642 | 197346.1246 | 36984.172 | 0 | 14400 | 0 | 0 | 40000 | 91384.172 | 149732.9658 | 66043.1642 | 0 | 14400 | 0 | 15567.3173 | 40000 | 136010.4815 | 222853.174 | 0 | 0 | 0 | 11000 | 0 | 0 | 40000 | 51000 | 83563.5 | 0 | 0 | 0 | 11000 | 0 | 0 | 0 | 11000 | 18023.5
Mall retail | 338180.2102 | 49590.7684 | 0 | 0 | 2021729.5175 | 0 | 0 | 2409500.4961 | 3947966.5628 | 4717368.8742 | 240129.6237 | 0 | 0 | 1200000 | 750000 | 6907498.4979 | 11317936.2888 | 2641726.5695 | 120064.8119 | 0 | 0 | 770000 | 750000 | 4281791.3814 | 7015715.1784 | 4717368.8742 | 240129.6237 | 0 | 0 | 2223902.4693 | 750000 | 7931400.9671 | 12995600.4846 | 172222.4 | 15069.46 | 0 | 0 | 2021729.5175 | 0 | 1500000 | 3709021.3775 | 6077231.527 | 338180.2102 | 14795.3842 | 0 | 0 | 2021729.5175 | 0 | 0 | 2374705.1119 | 3890954.3258
MULTI-UNIT RESIDENTIAL
Pre-2004 apartment - gas boiler | 422302.5375 | 289531.9688 | 0 | 0 | 1224065.326 | 0 | 0 | 1935899.8324 | 3171971.8753 | 4896261.3042 | 1835591.5572 | 240000 | 0 | 0 | 1250000 | 8221852.8614 | 13471505.9133 | 2741906.3304 | 917795.7786 | 240000 | 0 | 0 | 1250000 | 5149702.1089 | 8437786.9055 | 2981950 | 1835591.5572 | 84000 | 0 | 2019707.788 | 300000 | 7221249.3451 | 11832017.052 | 215062.722 | 73723.8446 | 0 | 0 | 1224065.326 | 0 | 1500000 | 3012851.8927 | 4936557.8262 | 422302.5375 | 144765.9844 | 0 | 0 | 1224065.326 | 0 | 0 | 1791133.848 | 2934772.8099
Pre-2004 apartment - electric | 0 | 289531.9688 | 180000 | 0 | 1196935.5415 | 0 | 0 | 1666467.5104 | 2730507.0158 | 0 | 1835591.5572 | 120000 | 0 | 0 | 250000 | 2205591.5572 | 3613861.7664 | 0 | 917795.7786 | 120000 | 0 | 0 | 250000 | 1287795.7786 | 2110053.3832 | 0 | 1835591.5572 | 90000 | 0 | 2019707.788 | 300000 | 4245299.3451 | 6955922.977 | 0 | 73723.8446 | 180000 | 0 | 1196935.5415 | 0 | 400000 | 1850659.3862 | 3032305.4043 | 0 | 0 | 0 | 0 | 1196935.5415 | 0 | 0 | 1196935.5415 | 1961178.8848
Post-2004 condo (window glazing alternate)
Post-2004 condo | 428009.3285 | 293444.563 | 0 | 0 | 1152376.9655 | 0 | 0 | 1873830.8571 | 3070271.8594 | 4962426.9975 | 1860396.8485 | 240000 | 0 | 0 | 1250000 | 8312823.846 | 13620561.8716 | 2778959.1186 | 930198.4242 | 240000 | 0 | 0 | 1250000 | 5199157.5428 | 8518819.6339 | 2849700 | 1860396.8485 | 96000 | 0 | 2047001.1365 | 300000 | 7153097.9849 | 11720351.0483 | 217968.975 | 74720.1128 | 0 | 0 | 1152376.9655 | 0 | 1500000 | 2945066.0534 | 4825490.7284 | 428009.3285 | 146722.2815 | 0 | 0 | 1152376.9655 | 0 | 0 | 1727108.5756 | 2829867.4011
RESIDENTIAL
Typical house (Pitched Roof)(Int. Wall Reno)
Typical house (Flat Roof)(Ext. Wall Reno) | 21000 | 5000 | 0 | 0 | 9800 | 0 | 0 | 35800 | 58658.3 | 12000 | 10000 | 0 | 0 | 0 | 10000 | 32000 | 52432 | 12000 | 10000 | 0 | 0 | 0 | 10000 | 32000 | 52432 | 6000 | 2500 | 0 | 0 | 22744.4571 | 10000 | 41244.4571 | 67579.0429 | 4843.755 | 1200 | 0 | 0 | 9800 | 2400 | 25000 | 43243.755 | 70854.8926 | 21000 | 2500 | 0 | 0 | 9800 | 0 | 0 | 33300 | 54562.05
INSTITUTIONAL
High water use hospital (inpatient) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39084675 | 9271790.6939 | 0 | 0 | 1200000 | 0 | 49556465.6939 | 81198269.0394 | 21887418 | 4635895.3469 | 0 | 0 | 1200000 | 0 | 27723313.3469 | 45424648.919 | 39084675 | 9271790.6939 | 0 | 0 | 18425632.5 | 84000 | 66866098.1939 | 109560101.8907 | 1962000 | 372387.8844 | 0 | 0 | 0 | 0 | 30000 | 2364387.8844 | 3874049.5486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Low water use hospital (outpatient) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38248000 | 2508617.5627 | 0 | 0 | 1200000 | 0 | 41956617.5627 | 68745917.8765 | 21418880 | 1254308.7814 | 0 | 0 | 1200000 | 0 | 23873188.7814 | 39116219.8183 | 38248000 | 2508617.5627 | 0 | 0 | 18031200 | 84000 | 58871817.5627 | 96461473.0765 | 1920000 | 100754.9478 | 0 | 0 | 0 | 0 | 30000 | 2050754.9478 | 3360161.9819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Assembly & educational | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on C6: Eric Chisholm: Plant Capacity (MBH) x Unitary cost ($/MBH)
Note on D6: Eric Chisholm: Plant Capacity (MBH) x Unitary cost ($/MBH)
Note on G6: Eric Chisholm: Plant Capacity (MBH) x Unitary cost ($/MBH)
Note on A23: User Note: This row is not used in this tab - no formulas are included in this row
Note on A27: User Note: This row is not used in this tab - no formulas are included in this row

## FS - Operational
Toronto 2030 District
Occupancy & Sub-Categories | HEATING LOADS BASIS (BASELINE) | [10 empty] | LIKE FOR LIKE RETROFIT (Base Case) | [8 empty] | ASHP RETROFIT | [7 empty] | ASHP w RNG BACKUP | [7 empty] | GSHP RETROFIT | [7 empty] | ELECTRIC RESISTANCE RETROFIT | [7 empty] | HYDROGEN CONVERSION RETROFIT | [7 empty] | LIKE FOR LIKE RETROFIT (Base Case) | ASHP RETROFIT | ASHP w RNG BACKUP | GSHP RETROFIT | ELECTRIC RESISTANCE RETROFIT | HYDROGEN CONVERSION RETROFIT
| EUI |  | Heat |  | Heating EUI |  | Baseline Heating Efficiency |  | Load |  |  | Heating Efficiency |  | Use |  | Operating Cost |  |  |  |  | Heating Efficiency |  | Use |  | Operating Cost |  |  |  | Heating Efficiency |  | Use |  | Operating Cost |  |  |  | Heating Efficiency |  | Use |  | Operating Cost |  |  |  | Heating Efficiency |  | Use |  | Operating Cost |  |  |  | Heating Efficiency |  | Use |  | Operating Cost |  |  |  | Annual Utility Cost | Annual Utility Cost | Annual Utility Cost | Annual Utility Cost | Annual Utility Cost | Annual Utility Cost
Units | Elec (ekWh/m²) | Gas (ekWh/m²) | Elec (%) | Gas (%) | Elec (ekWh/ft2) | Gas (ekWh/ft2) | Elec (%) | Gas (%) | Elec (ekWh_th/ft2) | Gas (ekWh_th/ft2) |  | Elec (%) | Gas (%) | Elec (kWh) | Gas (kWh) | Elec ($UI) | Gas ($UI) | Carbon Cost ($/ft²) | Total ($/ft²) |  | Elec (%) | Gas (%) | Elec (kWh) | Gas (kWh) | Elec ($UI) | Gas ($UI) | Carbon Cost ($/ft²) | Total ($/ft²) | Elec (%) | Gas (%) | Elec (kWh) | Gas (kWh) | Elec ($UI) | Gas ($UI) | Carbon Cost ($/ft²) | Total ($/ft²) | Elec (%) | Gas (%) | Elec (kWh) | Gas (kWh) | Elec ($UI) | Gas ($UI) | Carbon Cost ($/ft²) | Total ($/ft²) | Elec (%) | Gas (%) | Elec (kWh) | Gas (kWh) | Elec ($UI) | Gas ($UI) | Carbon Cost ($/ft²) | Total ($/ft²) | Elec (%) | Gas (%) | Elec (kWh) | Gas (kWh) | Elec ($UI) | Gas ($UI) | Carbon Cost ($/ft²) | Total ($/ft²) | $/ft² | $/ft² | $/ft² | $/ft² | $/ft² | $/ft²
OFFICE
Class 'A' - gas boiler | 12.2342 | 11.6737 | 0% | 100% | 0 | 11.6737 | 0% | 85% | 0 | 9.9227 |  | 0% | 85% | 0 | 11.6737 | 0 | 0.43887 | 0.54283 | 0.9817 |  | 280% | - | 3.5438 | 0 | 0.56701 | 0 | 0.041197 | 0.60821 | 280% | - | 3.5438 | 0 | 0.56701 | 0 | 0.041197 | 0.60821 | 310% | - | 3.2009 | 0 | 0.51214 | 0 | 0.03721 | 0.54935 | 98% | - | 10.1252 | 0 | 1.62 | 0 | 0.11771 | 1.7377 | 0% | 85% | 0 | 11.6737 | 0 | 2.218 | 0.19387 | 2.4119 | 0.9817 | 0.60821 | 0.60821 | 0.54935 | 1.7377 | 2.4119
Class 'A' - district heating/ cooling | 23.9079 | 0 | 50% | 0% | 11.954 | 0 | 98% | 0% | 11.7149 | 0 |  | 98% | 0% | 11.954 | 0 | 1.9126 | 0 | 0.13896 | 2.0516 |  | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | 2.0516 | 0 | 0 | 0 | 0 | 0
Class 'A' - electric | 23.9079 | 0 | 50% | 0% | 11.954 | 0 | 98% | 0% | 11.7149 | 0 |  | 98% | 0% | 11.954 | 0 | 1.9126 | 0 | 0.13896 | 2.0516 |  | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | 2.0516 | 0 | 0 | 0 | 0 | 0
Class 'B' & 'C' - rooftop units | 15.5349 | 11.6737 | 0% | 100% | 0 | 11.6737 | 0% | 75% | 0 | 8.7553 |  | 0% | 75% | 0 | 11.6737 | 0 | 0.43887 | 0.54283 | 0.9817 |  | 280% | - | 3.1269 | 0 | 0.5003 | 0 | 0.03635 | 0.53665 | 280% | - | 3.1269 | 0 | 0.5003 | 0 | 0.03635 | 0.53665 | 310% | - | 2.8243 | 0 | 0.45189 | 0 | 0.032832 | 0.48472 | 98% | - | 8.934 | 0 | 1.4294 | 0 | 0.10386 | 1.5333 | 0% | 75% | 0 | 11.6737 | 0 | 2.218 | 0.19387 | 2.4119 | 0.9817 | 0.53665 | 0.53665 | 0.48472 | 1.5333 | 2.4119
Class 'B' & 'C' - electric | 27.2087 | 0 | 50% | 0% | 13.6043 | 0 | 98% | 0% | 13.3322 | 0 |  | 98% | 0% | 13.6043 | 0 | 2.1767 | 0 | 0.15815 | 2.3348 |  | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | 2.3348 | 0 | 0 | 0 | 0 | 0
RETAIL & HOSPITALITY
Restaurant - gas MAU + RTU | 110.9698 | 31.0393 | 0% | 75% | 0 | 23.2795 | 0% | 75% | 0 | 17.4596 |  | 0% | 75% | 0 | 23.2795 | 0 | 0.87518 | 1.0825 | 1.9577 |  | 280% | - | 6.2356 | 0 | 0.99769 | 0 | 0.072489 | 1.0702 | 280% | - | 6.2356 | 0 | 0.99769 | 0 | 0.072489 | 1.0702 | 310% | - | 5.6321 | 0 | 0.90114 | 0 | 0.065474 | 0.96661 | 98% | - | 17.8159 | 0 | 2.8505 | 0 | 0.20711 | 3.0577 | 0% | 75% | 0 | 23.2795 | 0 | 4.4231 | 0.38661 | 4.8097 | 1.9577 | 1.0702 | 1.0702 | 0.96661 | 3.0577 | 4.8097
High-rise hotel - gas boiler | -1.5014 | 31.0393 | 0% | 75% | 0 | 23.2795 | 0% | 85% | 0 | 19.7876 |  | 0% | 75% | 0 | 26.3834 | 0 | 0.99188 | 1.2268 | 2.2187 |  | 280% | - | 7.067 | 0 | 1.1307 | 0 | 0.082154 | 1.2129 | 280% | - | 7.067 | 0 | 1.1307 | 0 | 0.082154 | 1.2129 | 310% | - | 6.3831 | 0 | 1.0213 | 0 | 0.074203 | 1.0955 | 98% | - | 20.1914 | 0 | 3.2306 | 0 | 0.23472 | 3.4653 | 0% | 75% | 0 | 26.3834 | 0 | 5.0128 | 0.43815 | 5.451 | 2.2187 | 1.2129 | 1.2129 | 1.0955 | 3.4653 | 5.451
High-rise hotel - electric | 29.5379 | 0 | 50% | 0% | 14.7689 | 0 | 98% | 0% | 14.4736 | 0 |  | 98% | 0% | 14.7689 | 0 | 2.363 | 0 | 0.17169 | 2.5347 |  | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | 2.5347 | 0 | 0 | 0 | 0 | 0
Standalone retail | -8.7912 | 31.0393 | 0% | 100% | 0 | 31.0393 | 0% | 75% | 0 | 23.2795 |  | 0% | 75% | 0 | 31.0393 | 0 | 1.1669 | 1.4433 | 2.6102 |  | 280% | - | 8.3141 | 0 | 1.3303 | 0 | 0.096651 | 1.4269 | 280% | - | 8.3141 | 0 | 1.3303 | 0 | 0.096651 | 1.4269 | 310% | - | 7.5095 | 0 | 1.2015 | 0 | 0.087298 | 1.2888 | 98% | - | 23.7546 | 0 | 3.8007 | 0 | 0.27615 | 4.0769 | 0% | 75% | 0 | 31.0393 | 0 | 5.8975 | 0.51547 | 6.4129 | 2.6102 | 1.4269 | 1.4269 | 1.2888 | 4.0769 | 6.4129
Mall retail | 1.3388 | 31.0393 | 0% | 100% | 0 | 31.0393 | 0% | 75% | 0 | 23.2795 |  | 0% | 75% | 0 | 31.0393 | 0 | 1.1669 | 1.4433 | 2.6102 |  | 280% | - | 8.3141 | 0 | 1.3303 | 0 | 0.096651 | 1.4269 | 280% | - | 8.3141 | 0 | 1.3303 | 0 | 0.096651 | 1.4269 | 310% | - | 7.5095 | 0 | 1.2015 | 0 | 0.087298 | 1.2888 | 98% | - | 23.7546 | 0 | 3.8007 | 0 | 0.27615 | 4.0769 | 0% | 75% | 0 | 31.0393 | 0 | 5.8975 | 0.51547 | 6.4129 | 2.6102 | 1.4269 | 1.4269 | 1.2888 | 4.0769 | 6.4129
MULTI-UNIT RESIDENTIAL
Pre-2004 apartment - gas boiler | 9.9385 | 11.7455 | 0% | 100% | 0 | 11.7455 | 0% | 85% | 0 | 9.9837 |  | 0% | 85% | 0 | 11.7455 | 0 | 0.44157 | 0.54617 | 0.98774 |  | 280% | - | 3.5656 | 0 | 0.5705 | 0 | 0.04145 | 0.61195 | 280% | - | 3.5656 | 0 | 0.5705 | 0 | 0.04145 | 0.61195 | 310% | - | 3.2205 | 0 | 0.51529 | 0 | 0.037439 | 0.55273 | 98% | - | 10.1874 | 0 | 1.63 | 0 | 0.11843 | 1.7484 | 0% | 85% | 0 | 11.7455 | 0 | 2.2316 | 0.19506 | 2.4267 | 0.98774 | 0.61195 | 0.61195 | 0.55273 | 1.7484 | 2.4267
Pre-2004 apartment - electric | 21.684 | 0 | 50% | 0% | 10.842 | 0 | 98% | 0% | 10.6252 | 0 |  | 98% | 0% | 10.842 | 0 | 1.7347 | 0 | 0.12604 | 1.8608 |  | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | na | na | 0 | 0 | 0 | 0 | 0 | 0 | 1.8608 | 0 | 0 | 0 | 0 | 0
Post-2004 condo (window glazing alternate) | [58 empty] | 0
Post-2004 condo | 9.9385 | 11.7455 | 0% | 100% | 0 | 11.7455 | 0% | 90% | 0 | 10.571 |  | 0% | 90% | 0 | 11.7455 | 0 | 0.44157 | 0.54617 | 0.98774 |  | 280% | - | 3.7753 | 0 | 0.60406 | 0 | 0.043888 | 0.64794 | 280% | - | 3.7753 | 0 | 0.60406 | 0 | 0.043888 | 0.64794 | 310% | - | 3.41 | 0 | 0.5456 | 0 | 0.039641 | 0.58524 | 98% | - | 10.7867 | 0 | 1.7259 | 0 | 0.1254 | 1.8513 | 0% | 90% | 0 | 11.7455 | 0 | 2.2316 | 0.19506 | 2.4267 | 0.98774 | 0.64794 | 0.64794 | 0.58524 | 1.8513 | 2.4267
RESIDENTIAL
Typical house (Pitched Roof)(Int. Wall Reno)
Typical house (Flat Roof)(Ext. Wall Reno) | 4.8931 | 11.7434 | 0% | 90% | 0 | 10.569 | 0% | 85% | 0 | 8.9837 | #REF! | 0% | 85% | 0 | 10.569 | 0 | 0.39734 | 0.49146 | 0.8888 | 97.5 | 280% | - | 3.2085 | 0 | 0.51335 | 0 | 0.037298 | 0.55065 | 280% | - | 3.2085 | 0 | 0.51335 | 0 | 0.037298 | 0.55065 | 310% | - | 2.898 | 0 | 0.46367 | 0 | 0.033689 | 0.49736 | 98% | - | 9.167 | 0 | 1.4667 | 0 | 0.10657 | 1.5733 | 0% | 85% | 0 | 10.569 | 0 | 2.0081 | 0.17552 | 2.1836 | 0.8888 | 0.55065 | 0.55065 | 0.49736 | 1.5733 | 2.1836
INSTITUTIONAL
High water use hospital (inpatient) | 61.7923 | 10.6327 | 0% | 90% | 0 | 9.5694 | 0% | 75% | 0 | 7.1771 |  | 0% | 75% | 0 | 9.5694 | 0 | 0.35976 | 0.44498 | 0.80474 |  | 280% | - | 2.5632 | 0 | 0.41012 | 0 | 0.029798 | 0.43992 | 280% | - | 2.5632 | 0 | 0.41012 | 0 | 0.029798 | 0.43992 | 310% | - | 2.3152 | 0 | 0.37043 | 0 | 0.026914 | 0.39734 | 98% | - | 7.3235 | 0 | 1.1718 | 0 | 0.085136 | 1.2569 | 0% | 75% | 0 | 9.5694 | 0 | 1.8182 | 0.15892 | 1.9771 | 0.80474 | 0.43992 | 0.43992 | 0.39734 | 1.2569 | 1.9771
Low water use hospital (outpatient) | 12.8915 | 10.6327 | 0% | 90% | 0 | 9.5694 | 0% | 75% | 0 | 7.1771 |  | 0% | 75% | 0 | 9.5694 | 0 | 0.35976 | 0.44498 | 0.80474 |  | 280% | - | 2.5632 | 0 | 0.41012 | 0 | 0.029798 | 0.43992 | 280% | - | 2.5632 | 0 | 0.41012 | 0 | 0.029798 | 0.43992 | 310% | - | 2.3152 | 0 | 0.37043 | 0 | 0.026914 | 0.39734 | 98% | - | 7.3235 | 0 | 1.1718 | 0 | 0.085136 | 1.2569 | 0% | 75% | 0 | 9.5694 | 0 | 1.8182 | 0.15892 | 1.9771 | 0.80474 | 0.43992 | 0.43992 | 0.39734 | 1.2569 | 1.9771
Assembly & educational | 28.5435 | 10.6327 | 0% | 90% | 0 | 9.5694 | 0% | 85% | 0 | 8.134 |  | 0% | 85% | 0 | 9.5694 | 0 | 0.35976 | 0.44498 | 0.80474 |  | 280% | - | 2.905 | 0 | 0.4648 | 0 | 0.033771 | 0.49857 | 280% | - | 2.905 | 0 | 0.4648 | 0 | 0.033771 | 0.49857 | 310% | - | 2.6239 | 0 | 0.41982 | 0 | 0.030503 | 0.45032 | 98% | - | 8.3 | 0 | 1.328 | 0 | 0.096488 | 1.4245 | 0% | 85% | 0 | 9.5694 | 0 | 1.8182 | 0.15892 | 1.9771 | 0.80474 | 0.49857 | 0.49857 | 0.45032 | 1.4245 | 1.9771
Note on AF7: User Note: Future research would benefit from allocating consumption between HP and gas consumption. The current analysis assumes the RNG backup never operates, and the HP system is used for 100% of heating annually
Note on C8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values assumed for this row are placeholders only.
Note on C15: User Note: Note that assumptions for these occupancy sub-categories result in negative values for electricity use. This is not an appropriate outcome for whole-building energy analysis. Since this analysis focuses on heating use, the cause was not investigated further.
Note on C17: User Note: Note that assumptions for these occupancy sub-categories result in negative values for electricity use. This is not an appropriate outcome for whole-building energy analysis. Since this analysis focuses on heating use, the cause was not investigated further.
Note on A23: User Note: This row is not used in this tab - no formulas are included in this row
Note on A27: User Note: This row is not used in this tab - no formulas are included in this row
Note on D31: User note: The institutional default assumptions/ inputs were not validated. Values for baseline gas use appear to be far lower than expected. We recommend validating before using these inputs.
Note on D32: User note: The institutional default assumptions/ inputs were not validated. Values for baseline gas use appear to be far lower than expected. We recommend validating before using these inputs.
Note on D33: User note: The institutional default assumptions/ inputs were not validated. Values for baseline gas use appear to be far lower than expected. We recommend validating before using these inputs.

## FS - Business Case
Toronto 2030 District
Occupancy & Sub-Categories | LIKE FOR LIKE RETROFIT (Base Case) |  |  |  |  | ASHP RETROFIT |  |  |  |  | ASHP w RNG BACKUP |  |  |  |  | GSHP RETROFIT |  |  |  |  | ELECTRIC RESISTANCE RETROFIT |  |  |  |  | HYDROGEN CONVERSION RETROFIT
| Total (Including M&L, Tax, PM, GC, …) | Amortized Capital Costs | Amortized Capital Costs | Total Cost | Incremental Cost | Total (Including M&L, Tax, PM, GC, …) | Amortized Capital Costs | Amortized Capital Costs | Total Cost | Incremental Cost | Total (Including M&L, Tax, PM, GC, …) | Amortized Capital Costs | Amortized Capital Costs | Total Cost | Incremental Cost | Total (Including M&L, Tax, PM, GC, …) | Amortized Capital Costs | Amortized Capital Costs | Total Cost | Incremental Cost | Total (Including M&L, Tax, PM, GC, …) | Amortized Capital Costs | Amortized Capital Costs | Total Cost | Incremental Cost | Total (Including M&L, Tax, PM, GC, …) | Amortized Capital Costs | Amortized Capital Costs | Total Cost | Incremental Cost
Units | $ | $/yr | $/yr/ft² | $/yr/ft² | $/yr/ft² | $ | $/yr | $/yr/ft² | $/yr/ft² | $/yr/ft² | $ | $/yr | $/yr/ft² | $/yr/ft² | $/yr/ft² | $ | $/yr | $/yr/ft² | $/yr/ft² | $/yr/ft² | $ | $/yr | $/yr/ft² | $/yr/ft² | $/yr/ft² | $ | $/yr | $/yr/ft² | $/yr/ft² | $/yr/ft²
OFFICE
Class 'A' - gas boiler | 4699265.9361 | 377081.2566 | 1.2511 | 2.2328 | 0 | 12617553.3708 | 820789.954 | 2.7234 | 3.3316 | 1.1 | 7518646.7328 | 489098.7598 | 1.6228 | 2.231 | 0 | 14471468.9419 | 941389.8224 | 3.1235 | 3.6728 | 1.44 | 6682942.8872 | 434735.0254 | 1.4424 | 3.1802 | 0.95 | 4605234.3084 | 299577.1006 | 0.99399 | 3.4059 | 1.17
Class 'A' - district heating/ cooling | 807489.1728 | 0 | 0 | 0 | 0 | 12027693.3708 | 0 | 0 | 0 | 0 | 7140153.2328 | 0 | 0 | 0 | 0 | 14471468.9419 | 0 | 0 | 0 | 0 | 3192060.7584 | 0 | 0 | 0 | 0 | 585571.3892 | 0 | 0 | 0 | 0
Class 'A' - electric | 737325 | 0 | 0 | 0 | 0 | 1961516.8123 | 0 | 0 | 0 | 0 | 1392725 | 0 | 0 | 0 | 0 | 5435963.7006 | 0 | 0 | 0 | 0 | 1392725 | 0 | 0 | 0 | 0 | 737325 | 0 | 0 | 0 | 0
Class 'B' & 'C' - rooftop units | 371529.875 | 29812.5184 | 0.82431 | 1.806 | 0 | 2270526.5089 | 147701.0078 | 4.0839 | 4.6921 | 2.89 | 1594260.5 | 103708.9334 | 2.8675 | 3.4757 | 1.67 | 2155396.2936 | 140211.6221 | 3.8768 | 4.4262 | 2.62 | 1221553.6401 | 79463.8173 | 2.1972 | 3.9349 | 2.13 | 418636.75 | 27232.9214 | 0.75298 | 3.1649 | 1.36
Class 'B' & 'C' - electric | 88479 | 0 | 0 | 0 | 0 | 376855 | 0 | 0 | 0 | 0 | 373578 | 0 | 0 | 0 | 0 | 819754.4356 | 0 | 0 | 0 | 0 | 215514.6401 | 0 | 0 | 0 | 0 | 88479 | 0 | 0 | 0 | 0
RETAIL & HOSPITALITY
Restaurant - gas MAU + RTU | 181217.7824 | 14541.3837 | 9.6496 | 11.6073 | 0 | 751720.7223 | 48900.5118 | 32.4501 | 33.0583 | 21.45 | 682915.2612 | 44424.6178 | 29.4799 | 30.0881 | 18.48 | 981233.6556 | 63830.6574 | 42.3576 | 42.907 | 31.3 | 724660.3453 | 47140.1954 | 31.2819 | 33.0197 | 21.41 | 145498.6412 | 9464.8954 | 6.2808 | 11.0906 | -0.52
High-rise hotel - gas boiler | 3165126.0035 | 253977.8993 | 1.0725 | 3.2912 | 0 | 13612244.3391 | 885496.0289 | 3.7393 | 4.3475 | 1.06 | 8517369.1293 | 554067.085 | 2.3398 | 2.948 | -0.34 | 16575249.9997 | 1078243.7993 | 4.5533 | 5.1026 | 1.81 | 4924719.0302 | 320360.0403 | 1.3528 | 3.0906 | -0.2 | 2928937.3515 | 190531.578 | 0.80459 | 6.2556 | 2.96
High-rise hotel - electric | 749613.75 | 0 | 0 | 0 | 0 | 3519125.0102 | 0 | 0 | 0 | 0 | 2021722.5051 | 0 | 0 | 0 | 0 | 6809830.6709 | 0 | 0 | 0 | 0 | 1405013.75 | 0 | 0 | 0 | 0 | 626726.25 | 0 | 0 | 0 | 0
Standalone retail | 18023.5 | 1446.2523 | 0.95972 | 3.57 | 0 | 197346.1246 | 12837.6486 | 8.519 | 9.1272 | 5.56 | 149732.9658 | 9740.3443 | 6.4636 | 7.0718 | 3.5 | 222853.174 | 14496.9188 | 9.6201 | 10.1694 | 6.6 | 83563.5 | 5435.9256 | 3.6072 | 5.345 | 1.78 | 18023.5 | 1172.4545 | 0.77803 | 7.191 | 3.62
Mall retail | 3947966.5628 | 316795.0511 | 1.4716 | 4.0818 | 0 | 11317936.2888 | 736247.9977 | 3.42 | 4.0282 | -0.05 | 7015715.1784 | 456382.3405 | 2.12 | 2.7282 | -1.35 | 12995600.4846 | 845382.4613 | 3.9269 | 4.4763 | 0.39 | 6077231.527 | 395332.6321 | 1.8364 | 3.5741 | -0.51 | 3890954.3258 | 253112.1627 | 1.1757 | 7.5887 | 3.51
MULTI-UNIT RESIDENTIAL
Pre-2004 apartment - gas boiler | 3171971.8753 | 254527.2298 | 1.0652 | 2.0529 | 0 | 13471505.9133 | 876340.7924 | 3.6673 | 4.2755 | 2.22 | 8437786.9055 | 548890.1471 | 2.297 | 2.9052 | 0.85 | 11832017.052 | 769689.6891 | 3.221 | 3.7704 | 1.72 | 4936557.8262 | 321130.1709 | 1.3439 | 3.0816 | 1.03 | 2934772.8099 | 190911.1829 | 0.79893 | 3.2256 | 1.17
Pre-2004 apartment - electric | 2730507.0158 | 0 | 0 | 0 | 0 | 3613861.7664 | 0 | 0 | 0 | 0 | 2110053.3832 | 0 | 0 | 0 | 0 | 6955922.977 | 0 | 0 | 0 | 0 | 3032305.4043 | 0 | 0 | 0 | 0 | 1961178.8848 | 0 | 0 | 0 | 0
Post-2004 condo (window glazing alternate)
Post-2004 condo | 3070271.8594 | 246366.5574 | 1.0173 | 2.005 | 0 | 13620561.8716 | 886037.0963 | 3.6585 | 4.2667 | 2.26 | 8518819.6339 | 554161.4424 | 2.2881 | 2.8964 | 0.89 | 11720351.0483 | 762425.6553 | 3.1481 | 3.6974 | 1.69 | 4825490.7284 | 313905.0969 | 1.2961 | 3.0339 | 1.03 | 2829867.4011 | 184086.9355 | 0.7601 | 3.1868 | 1.18
RESIDENTIAL
Typical house (Pitched Roof)(Int. Wall Reno)
Typical house (Flat Roof)(Ext. Wall Reno) | 58658.3 | 4706.8938 | 1.9435 | 2.8323 | 0 | 52432 | 3410.7768 | 1.4083 | 2.0165 | -0.82 | 52432 | 3410.7768 | 1.4083 | 2.0165 | -0.82 | 67579.0429 | 4396.1137 | 1.8152 | 2.3645 | -0.47 | 70854.8926 | 4609.2124 | 1.9032 | 3.6409 | 0.81 | 54562.05 | 3549.3397 | 1.4655 | 3.6492 | 0.82
INSTITUTIONAL
High water use hospital (inpatient) | 0 | 0 | 0 | 0 | 0 | 81198269.0394 | 5282063.927 | 4.3971 | 5.0053 | 5.01 | 45424648.919 | 2954938.6002 | 2.4599 | 3.0681 | 3.07 | 109560101.8907 | 7127041.8555 | 5.933 | 6.4824 | 6.48 | 3874049.5486 | 252012.4827 | 0.20979 | 1.9475 | 1.95 | 0 | 0 | 0 | 0 | 0
Low water use hospital (outpatient) | 0 | 0 | 0 | 0 | 0 | 68745917.8765 | 4472020.6138 | 13.7594 | 14.3676 | 14.37 | 39116219.8183 | 2544566.2341 | 7.8291 | 8.4373 | 8.44 | 96461473.0765 | 6274957.2536 | 19.3066 | 19.856 | 19.86 | 3360161.9819 | 218583.359 | 0.67253 | 2.4103 | 2.41 | 0 | 0 | 0 | 0 | 0
Assembly & educational | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on D4: User Note: If the base case is not a gas retrofit, it will likely not be suitable for this conversion and won't be calculated further.
Note on J4: User Note: If the base case is not a gas retrofit, it will likely not be suitable for this conversion and won't be calculated further.
Note on P4: User Note: If the base case is not a gas retrofit, it will likely not be suitable for this conversion and won't be calculated further.
Note on V4: User Note: If the base case is not a gas retrofit, it will likely not be suitable for this conversion and won't be calculated further.
Note on AB4: User Note: If the base case is not a gas retrofit, it will likely not be suitable for this conversion and won't be calculated further.
Note on AH4: User Note: If the base case is not a gas retrofit, it will likely not be suitable for this conversion and won't be calculated further.
Note on D8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values calculated as $0 in this row.
Note on J8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values calculated as $0 in this row.
Note on P8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values calculated as $0 in this row.
Note on V8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values calculated as $0 in this row.
Note on AB8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values calculated as $0 in this row.
Note on AH8: User Note: District energy conversion is not evaluated by this tool. See methodology. Values calculated as $0 in this row.
Note on D9: User Note: Electric conversion is not evaluated by this tool. See methodology. Values calculated as $0 in the applicable rows
Note on J9: User Note: Electric conversion is not evaluated by this tool. See methodology. Values calculated as $0 in the applicable rows
Note on P9: User Note: Electric conversion is not evaluated by this tool. See methodology. Values calculated as $0 in the applicable rows
Note on V9: User Note: Electric conversion is not evaluated by this tool. See methodology. Values calculated as $0 in the applicable rows
Note on AB9: User Note: Electric conversion is not evaluated by this tool. See methodology. Values calculated as $0 in the applicable rows
Note on AH9: User Note: Electric conversion is not evaluated by this tool. See methodology. Values calculated as $0 in the applicable rows
Note on A23: User Note: This row is not used in this tab - no formulas are included in this row
Note on A27: User Note: This row is not used in this tab - no formulas are included in this row

## FS - Graphical Analyses
Toronto 2030 District
Building Typology and Fuel Switching Graphical Analysis
This tab contains two graphs. To view each graph collapse/expand rows either using the [+] icons at rows 44 and 85 , or the [1]/[2] icon in the top-left corner.
Baseline Calibrated Energy Uses (eGWh) per Building Type
Description of Graphic:
Comparison of how much energy each building sub-occupancy is expected to use based on the associated baseline predicted energy use and the measured energy. Data points can be found in the [Building Typology] tab.
97.5
Relative Costs by Typology ($/ft2)
Description of Graphic:
Shows and compares the calculated total costs ($/yr/ft²) from the [FS - Business Case] tab for each retrofit versus the base case for all sub-occupancy types in this tool.

## Efficiency
Toronto 2030 District
Occupancy & Sub-Categories | Building Form and Massing | [11 empty] | Baseline Building Measures | [9 empty] | BAU Replacement Measures | [29 empty] | Distributed Energy Resource Measures
| Floor Height | # Floors Subgrade | Window/ Wall Ratio | Exterior Party Walls | Length to Width Ratio | Exterior Perimeter | Envelope Area | Wall Area | Window Area | Wall SubGrade | Roof Area | Slab Area on Grade | Wall RSI | Wall Heat Loss | Wall Peak Heat Loss | Window RSI | Window Heat Loss | Window Peak Heat Loss | Roof RSI | Roof Heat Loss | Roof Peak Heat Loss | Baseline Annual Heat Loss | Wall RSI | Wall Cost | Wall Cost | Wall Heat Loss | Wall Heat Loss Savings | Wall Peak Heat Loss | Wall Heating Peak Savings | Wall Heating Peak Reduction | Wall Cooling Peak Savings | Wall Cooling Peak Reduction | Window RSI | Window Cost | Window Cost | Window Heat Loss | Window Heat Loss Savings | Window Peak Heat Loss | Window Heating Peak Savings | Window Heating Peak Reduction | Window Cooling Peak Savings | Window Cooling Peak Reduction | Roof RSI | Roof Cost | Roof Cost | Roof Heat Loss | Roof Heat Loss Savings | Roof Peak Heat Loss | Roof Heating Peak Savings | Roof Heating Peak Reduction | Roof Cooling Peak Savings | Roof Cooling Peak Reduction | Wall RSI | Wall Cost | Wall Cost | Wall Heat Loss | Window Heat Loss Savings | Wall Peak Heat Loss | Wall Heating Peak Savings | Wall Heating Peak Reduction | Wall Cooling Peak Savings | Wall Cooling Peak Reduction | Window RSI | Window Cost | Window Cost | Window Heat Loss | Window Heat Loss Savings | Window Peak Heat Loss | Window Heating Peak Savings | Window Heating Peak Reduction | Window Cooling Peak Savings | Window Cooling Peak Reduction | Roof RSI | Roof Cost | Roof Cost | Roof Heat Loss | Roof Heat Loss Savings | Roof Peak Heat Loss | Roof Heating Peak Savings | Roof Heating Peak Reduction | Roof Cooling Peak Savings | Roof Cooling Peak Reduction | Available Cost-effective Max ERV Efficiency | ERV Cost | Estimated CFM | Heating Peak Reduction | Heating Peak Reduction | Baseline Heating Size for Fresh Air | % of Total Plant Size | DER Annual Heat Loss | Change in Annual Heat Loss
Units | m | N/A | % Window | % | # L/W | m | m² | m² | m² | m² | m² | m² | m2·K/W | GJ | kW | m2·K/W | GJ | kW | m2·K/W | GJ | kW | GJ | m2·K/W | $/ft2 | $ | GJ | GJ | kW | kW | % | kW | % | m2·K/W | $/ft2 | $ | GJ | GJ | kW | kW | % | kW | % | m2·K/W | $/ft2 | $ | GJ | GJ | kW | kW | % | kW | % | m2·K/W | $/ft2 | $ | GJ | GJ | kW | kW | % | kW | % | m2·K/W | $/ft2 | $ | GJ | GJ | kW | kW | % | kW | % | m2·K/W | $/ft2 | $ | GJ | GJ | kW | kW | % | kW | % | % | $ | CFM | kW | % | kW | % | GJ | GJ
OFFICE
Class 'A' - gas boiler | 3.8 | 3 | 100% | 0% | 1 | 149.6663 | 11374.6385 | 0 | 11374.6385 | 448.9989 | 1400 | 1400 |  | 0 | 0 | 0.35 | 12074.0066 | 1364.9566 | 1.2327 | 421.9417 | 47.7002 | 12495.9483 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0.55 | 170.9418 | 20929334.7587 | 7683.4649 | 4390.5417 | 868.6088 | 496.3479 | 20.57% | 118.1781 | 4.353% | 1.2327 | 28.8 | 434000 | 421.9421 | -0.00033755 | 47.7002 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0.7 | 212.8225 | 26057021.7745 | 6037.0081 | 6036.9985 | 682.4783 | 682.4783 | 28.28% | 162.4948 | 5.985% | 6.1635 | 78.9677 | 1190000 | 84.3884 | 337.5533 | 9.54 | 38.1601 | 1.581% | 9.0857 | 0.3347% | 85% | 531600 | 29000 | 591.6 | 0.24536 | 696 | 28.87% | 6121.3965 | -6374.5518
Class 'A' - district heating/ cooling | 3.8 | 3 | 100% | 0% | 1 | 149.6663 | 11374.6385 | 0 | 11374.6385 | 448.9989 | 1400 | 1400 |  | 0 | 0 | 0.35 | 12074.0066 | 1364.9566 | 1.2327 | 421.9417 | 47.7002 | 12495.9483 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0.55 | 170.9418 | 20929334.7587 | 7683.4649 | 4390.5417 | 868.6088 | 496.3479 | 20.57% | 118.1781 | 4.353% | 1.2327 | 28.8 | 434000 | 421.9421 | -0.00033755 | 47.7002 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0.7 | 212.8225 | 26057021.7745 | 6037.0081 | 6036.9985 | 682.4783 | 682.4783 | 28.28% | 162.4948 | 5.985% | 6.1635 | 78.9677 | 1190000 | 84.3884 | 337.5533 | 9.54 | 38.1601 | 1.581% | 9.0857 | 0.3347% | 85% | 531600 | 29000 | 591.6 | 0.24536 | 696 | 28.87% | 6121.3965 | -6374.5518
Class 'A' - electric | 3.8 | 3 | 100% | 0% | 1 | 149.6663 | 11374.6385 | 0 | 11374.6385 | 448.9989 | 1400 | 1400 |  | 0 | 0 | 0.35 | 12074.0066 | 1364.9566 | 1.2327 | 421.9417 | 47.7002 | 12495.9483 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0.55 | 170.9418 | 20929334.7587 | 7683.4649 | 4390.5417 | 868.6088 | 496.3479 | 20.57% | 118.1781 | 4.353% | 1.2327 | 28.8 | 434000 | 421.9421 | -0.00033755 | 47.7002 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0% | 0.7 | 212.8225 | 26057021.7745 | 6037.0081 | 6036.9985 | 682.4783 | 682.4783 | 28.28% | 162.4948 | 5.985% | 6.1635 | 78.9677 | 1190000 | 84.3884 | 337.5533 | 9.54 | 38.1601 | 1.581% | 9.0857 | 0.3347% | 85% | 531600 | 29000 | 591.6 | 0.24536 | 696 | 28.87% | 6121.3965 | -6374.5518
Class 'B' & 'C' - rooftop units | 3.8 | 3 | 60% | 0% | 1 | 94.6573 | 2158.1859 | 863.2744 | 1294.9115 | 283.9718 | 560 | 560 | 1.7 | 188.6608 | 21.328 | 0.27 | 1781.7969 | 201.4307 | 1.2327 | 168.7767 | 19.0801 | 2139.2344 | 6.6 | 20.9032 | 194236.7314 | 48.5945 | 140.0663 | 5.4936 | 15.8344 | 3.978% | 3.7701 | 1.194% | 1.2 | 148.645 | 2071858.4687 | 400.9046 | 1380.8922 | 45.3219 | 156.1088 | 39.22% | 37.1688 | 11.78% | 1.2327 | 26.4774 | 159600 | 168.7768 | -0.00013502 | 19.0801 | 0 | 0% | 0 | 0% | 6.6 | 86.66 | 805262.3248 | 48.5945 | 140.0663 | 5.4936 | 15.8344 | 3.978% | 3.7701 | 1.194% | 0.93 | 198.4318 | 2765801.5645 | 517.2963 | 1264.5006 | 58.4799 | 142.9508 | 35.92% | 34.0359 | 10.78% | 5.8 | 72.3715 | 436240 | 35.8709 | 132.9058 | 4.0552 | 15.0249 | 3.775% | 3.5774 | 1.133% | 70% | 776550 | 4000 | 67.2 | 0.16891 | 96 | 24.13% | 601.7617 | -1537.4727
Class 'B' & 'C' - electric | 3.8 | 3 | 60% | 0% | 1 | 94.6573 | 2158.1859 | 863.2744 | 1294.9115 | 283.9718 | 560 | 560 | 1.7 | 188.6608 | 21.328 | 0.27 | 1781.7969 | 201.4307 | 1.2327 | 168.7767 | 19.0801 | 2139.2344 | 6.6 | 20.9032 | 194236.7314 | 48.5945 | 140.0663 | 5.4936 | 15.8344 | 3.978% | 3.7701 | 1.194% | 1.2 | 148.645 | 2071858.4687 | 400.9046 | 1380.8922 | 45.3219 | 156.1088 | 39.22% | 37.1688 | 11.78% | 1.2327 | 26.4774 | 159600 | 168.7768 | -0.00013502 | 19.0801 | 0 | 0% | 0 | 0% | 6.6 | 86.66 | 805262.3248 | 48.5945 | 140.0663 | 5.4936 | 15.8344 | 3.978% | 3.7701 | 1.194% | 0.93 | 198.4318 | 2765801.5645 | 517.2963 | 1264.5006 | 58.4799 | 142.9508 | 35.92% | 34.0359 | 10.78% | 5.8 | 72.3715 | 436240 | 35.8709 | 132.9058 | 4.0552 | 15.0249 | 3.775% | 3.5774 | 1.133% | 70% | 776550 | 4000 | 67.2 | 0.16891 | 96 | 24.13% | 601.7617 | -1537.4727
RETAIL & HOSPITALITY
Restaurant - gas MAU + RTU | 4 | 0 | 50% | 50% | 1 | 23.6643 | 94.6573 | 47.3286 | 47.3286 | 0 | 140 | 140 | 0.36 | 48.8431 | 5.5217 | 0.16 | 109.897 | 12.4238 | 1.2327 | 42.1942 | 4.77 | 200.9343 | 3.1 | 51 | 25981.4772 | 5.6721 | 43.171 | 0.64123 | 4.8804 | 3.904% | 1.162 | 1.441% | 0.63 | 58.0645 | 29580.3989 | 27.9104 | 81.9866 | 3.1552 | 9.2685 | 7.415% | 2.2068 | 2.736% | 1.2327 | 24.6193 | 37100 | 42.1942 | -3.3755e-05 | 4.77 | 0 | 0% | 0 | 0% | 3.1 | 30.1935 | 15381.81 | 5.6721 | 43.171 | 0.64123 | 4.8804 | 3.904% | 1.162 | 1.441% | 0.63 | 85.9354 | 43778.9904 | 27.9104 | 81.9866 | 3.1552 | 9.2685 | 7.415% | 2.2068 | 2.736% | 5.8 | 69.6773 | 105000 | 8.9677 | 33.2264 | 1.0138 | 3.7562 | 3.005% | 0.89434 | 1.109% | 85% | 16900 | 1506.946 | 30.7417 | 0.24703 | 36.1667 | 29.06% | 42.5502 | -158.3841
High-rise hotel - gas boiler | 3 |  | 40% |  | 1 | 132.665 | 7959.8995 | 4775.9397 | 3183.9598 | 0 | 1100 | 1100 | 1.7 | 1043.7386 | 117.9938 | 0.27 | 4381.1252 | 495.2826 | 1.2327 | 331.5257 | 37.4787 | 5756.3895 | 5.7 | 51.0967 | 2626766.834 | 311.2907 | 732.4479 | 35.1911 | 82.8027 | 3.774% | 19.7149 | 1.386% | 0.93 | 148.645 | 5094335.678 | 1271.9406 | 3109.1846 | 143.7917 | 351.4909 | 281.2% | 83.6883 | 5.885% | 1.2327 | 28.8 | 341000 | 331.5259 | -0.00026522 | 37.4787 | 0 | 0% | 0 | 0% | 5.7 | 30.1935 | 1552180.4019 | 311.2907 | 732.4479 | 35.1911 | 82.8027 | 3.774% | 19.7149 | 1.386% | 0.93 | 198.4318 | 6800619.7341 | 1271.9406 | 3109.1846 | 143.7917 | 351.4909 | 281.2% | 83.6883 | 5.885% | 5.8 | 78.9212 | 934450 | 70.4607 | 261.065 | 7.9655 | 29.5132 | 23.61% | 7.0269 | 0.4941% | 82% | 627640 | N/A, per suite units | 431.5128 | 0.19688 | 526.2351 | 24.01% | 1653.692 | -4102.6975
High-rise hotel - electric | 3 |  | 40% |  | 1 | 132.665 | 7959.8995 | 4775.9397 | 3183.9598 | 0 | 1100 | 1100 | 1.7 | 1043.7386 | 117.9938 | 0.27 | 4381.1252 | 495.2826 | 1.2327 | 331.5257 | 37.4787 | 5756.3895 | 5.7 | 51.0967 | 2626766.834 | 311.2907 | 732.4479 | 35.1911 | 82.8027 | 3.774% | 19.7149 | 1.386% | 0.93 | 148.645 | 5094335.678 | 1271.9406 | 3109.1846 | 143.7917 | 351.4909 | 281.2% | 83.6883 | 5.885% | 1.2327 | 28.8 | 341000 | 331.5259 | -0.00026522 | 37.4787 | 0 | 0% | 0 | 0% | 5.7 | 30.1935 | 1552180.4019 | 311.2907 | 732.4479 | 35.1911 | 82.8027 | 3.774% | 19.7149 | 1.386% | 0.93 | 198.4318 | 6800619.7341 | 1271.9406 | 3109.1846 | 143.7917 | 351.4909 | 281.2% | 83.6883 | 5.885% | 5.8 | 78.9212 | 934450 | 70.4607 | 261.065 | 7.9655 | 29.5132 | 23.61% | 7.0269 | 0.4941% | 82% | 1171300 | N/A, per suite units | 431.5128 | 0.19688 | 526.2351 | 24.01% | 1653.692 | -4102.6975
Standalone retail | 4 |  | 50% | 50% | 1 | 23.6643 | 94.6573 | 47.3286 | 47.3286 | 0 | 140 | 140 | 0.36 | 48.8431 | 5.5217 | 0.16 | 109.897 | 12.4238 | 1.2327 | 42.1942 | 4.77 | 200.9343 | 3.1 | 51 | 25981.4772 | 5.6721 | 43.171 | 0.64123 | 4.8804 | 34.86% | 1.162 | 7% | 0.63 | 70.1419 | 35733.1219 | 27.9104 | 81.9866 | 3.1552 | 9.2685 | 66.2% | 2.2068 | 13.29% | 1.2327 | 24.6193 | 37100 | 42.1942 | -3.3755e-05 | 4.77 | 0 | 0% | 0 | 0% | 3.1 | 30.1935 | 15381.8074 | 5.6721 | 43.171 | 0.64123 | 4.8804 | 34.86% | 1.162 | 7% | 0.63 | 85.9911 | 43807.3876 | 27.9104 | 81.9866 | 3.1552 | 9.2685 | 66.2% | 2.2068 | 13.29% | 5.8 | 69.6773 | 105000 | 8.9677 | 33.2264 | 1.0138 | 3.7562 | 26.83% | 0.89434 | 5.388% | 82% | 142000 | 203.4377 | 4.0037 | 0.2952 | 4.8825 | 36% | 42.5502 | -158.3841
Mall retail | 4 |  | 100% |  | 1 | 400 | 3200 | 0 | 3200 | 0 | 10000 | 10000 | [70 empty] | 85% |  | 29062.53 | 592.8756 | 0.34425 | 697.5007 | 40.5% | 0 | 0
MULTI-UNIT RESIDENTIAL | [10 empty] | 0 | 0
Pre-2004 apartment - gas boiler | 3 |  | 60% |  | 0.31142 | 202.1546 | 7277.5665 | 2911.0266 | 4366.5399 | 0 | 1850 | 1850 | 0.8 | 1351.8797 | 152.8289 | 0.27 | 6008.3541 | 679.2395 | 1.2327 | 557.5659 | 63.0324 | 7917.7996 | 1.5 | 20.9032 | 654980.9824 | 721.0031 | 630.8766 | 81.5087 | 71.3202 | 3.977% | 16.981 | 1.183% | 0.93 | 148.645 | 6986463.8127 | 1744.3623 | 4263.9918 | 197.1986 | 482.041 | 26.88% | 114.7717 | 7.998% | 1.2327 | 28.8 | 573500 | 557.5663 | -0.00044605 | 63.0324 | 0 | 0% | 0 | 0% | 6.6 | 42.7354 | 1339072.2308 | 163.8643 | 1188.0153 | 18.5247 | 134.3042 | 7.489% | 31.9772 | 2.228% | 0.93 | 189.9312 | 8926954.1366 | 1744.3623 | 4263.9918 | 197.1986 | 482.041 | 26.88% | 114.7717 | 7.998% | 5.8 | 30.1935 | 601250 | 118.5021 | 439.0638 | 13.3966 | 49.6358 | 2.768% | 11.8181 | 0.8236% | 82% | 875004 | N/A, per suite units | 235.1352 | 0.10933 | 286.7503 | 13.33% | 2026.7287 | -5891.071
Pre-2004 apartment - electric | 3 |  | 60% |  | 1 | 172.0465 | 6193.6742 | 2477.4697 | 3716.2045 | 0 | 1850 | 1850 | 2.1 | 438.2994 | 49.5494 | 0.27 | 5113.4933 | 578.0763 | 1.2327 | 557.5659 | 63.0324 | 6109.3586 | 6.6 | 20.9032 | 557430.6773 | 139.459 | 298.8404 | 15.7657 | 33.7837 | 1.57% | 8.0437 | 0.5605% | 0.93 | 148.645 | 5945927.2246 | 1484.5638 | 3628.9296 | 167.8286 | 410.2477 | 19.06% | 97.678 | 6.807% | 1.2327 | 28.8 | 573500 | 557.5663 | -0.00044605 | 63.0324 | 0 | 0% | 0 | 0% | 0.7 | 42.7354 | 1139636.0514 | 1314.8993 | -876.5999 | 148.6482 | -99.0988 | -4.605% | -23.5949 | -1.644% | 0.93 | 189.9312 | 7597408.5112 | 1484.5638 | 3628.9296 | 167.8286 | 410.2477 | 19.06% | 97.678 | 6.807% | 5.8 | 30.1935 | 601250 | 118.5021 | 439.0638 | 13.3966 | 49.6358 | 2.306% | 11.8181 | 0.8236% | 82% | 866639 | N/A, per suite units | 235.1352 | 0.10933 | 286.7503 | 13.33% | 2917.9652 | -3191.3935
Post-2004 condo (window glazing alternate) | 2.6 | 0 | 100% | 0% | 1 | 109.5445 | 8544.4719 | 0 | 8544.4719 | 0 | 750 | 750 | 0.7 | 0 | 0 | 0.27 | 11757.1839 | 1329.1401 | 1.2327 | 226.0402 | 25.5537 | 11983.2241 | 3.1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.93 | 26.0129 | 2392452.1312 | 3413.3787 | 8343.8052 | 385.8794 | 943.2607 | 43.23% | 224.5859 |  |  | 0 | 0 |  | 226.0402 |  | 25.5537 |  |  |  | 0 | 0 | 0 | [7 empty] | 0.93 | 29.729 | 2734231.0071 | 3413.3787 | 8343.8052 | 385.8794 | 943.2607 |  | 224.5859 | [12 empty] | 1122608 | [5 empty] | 3413.3787 | -8569.8454
Post-2004 condo | 2.6 |  | 80% |  | 1 | 109.5445 | 8544.4719 | 1708.8944 | 6835.5775 | 0 | 750 | 750 | 0.7 | 906.9828 | 102.5337 | 0.27 | 9405.7471 | 1063.3121 | 1.2327 | 226.0402 | 25.5537 | 10538.7701 | 3.1 | 183.9482 | 3383610.8712 | 204.8027 | 702.18 | 23.1528 | 79.3809 | 3.638% | 18.9002 | 1.399% | 0.88 | 148.645 | 10936924.0283 | 2885.8565 | 6519.8906 | 326.2435 | 737.0686 | 33.78% | 175.4925 | 12.99% | 5.8 | 30.658 | 247500 | 48.0414 | 177.9988 | 5.431 | 20.1226 | 0.9222% | 4.7911 | 0.3546% | 3.1 | 219.9203 | 4045294.775 | 204.8027 | 702.18 | 23.1528 | 79.3809 | 3.638% | 18.9002 | 1.399% | 0.88 | 189.9312 | 13974654.6771 | 2885.8565 | 6519.8906 | 326.2435 | 737.0686 | 33.78% | 175.4925 | 12.99% | 5.8 | 30.1935 | 243750 | 48.0414 | 177.9988 | 5.431 | 20.1226 | 0.9222% | 4.7911 | 0.3546% | 82% |  | N/A, per suite units | 301.6617 | 0.1384 | 367.8801 | 16.88% | 3138.7006 | -7400.0695
RESIDENTIAL
Typical house (Pitched Roof)(Int. Wall Reno) | 3 | 0.5 | 20% | 25% | 1 | 28.4605 | 213.4537 | 170.763 | 42.6907 | 14.2302 | 100.6231 | 90 | 0.6 | 105.7364 | 11.9534 | 0.27 | 58.7424 | 6.6408 | 4.2 | 8.9008 | 1.0062 | 173.3796 | 2.1 | 21 | 38599.5915 | 30.2104 | 75.5259 | 3.4153 | 8.5381 | 35.58% | 2.0329 | 15.97% | 0.77 | 44.129 | 20278.1055 | [7 empty] | 13.2 | 13 | 14080.2551 | 2.8321 | 6.0687 | 0.32016 | 0.68607 | 2.859% | 0.16335 | 1.283% | 2.1 | 12.5419 | 23053.0041 | 30.2104 | 75.5259 | 3.4153 | 8.5381 | 35.58% | 2.0329 | 15.97% |  | 53.4193 | 24547.1803 | [7 empty] | 13.2 | 4.4346 | 4803.074 | 2.8321 | 6.0687 | 0.32016 | 0.68607 | 2.859% | 0.16335 | 1.283% |  | 3500 | [5 empty] | 33.0425 | -140.3371
Typical house (Flat Roof)(Ext. Wall Reno) | 3 | 0.5 | 20% | 25% | 1 | 28.4605 | 213.4537 | 170.763 | 42.6907 | 14.2302 | 90 | 90 | 0.6 | 105.7364 | 11.9534 | 0.27 | 58.7424 | 6.6408 | 4.2 | 7.9611 | 0.9 | 172.4399 | 3.1 | 21 | 38599.5915 | 20.4651 | 85.2712 | 2.3136 | 9.6398 | 40.17% | 2.2952 | 18.03% | 0.77 | 44.129 | 20278.1055 | 20.598 | 38.1444 | 2.3286 | 4.3122 | 17.97% | 1.0267 | 8.065% | 13.2 | 13 | 12593.763 | 2.5331 | 5.428 | 0.28636 | 0.61364 | 2.557% | 0.1461 | 1.148% | 3.1 | 15.329 | 28175.894 | 20.4651 | 85.2712 | 2.3136 | 9.6398 | 40.17% | 2.2952 | 18.03% | 1.04 | 53.4193 | 24547.1803 | 15.2504 | 43.492 | 1.724 | 4.9167 | 20.49% | 1.1707 | 9.196% | 11.2 | 17.9768 | 17415 | 2.9854 | 4.9757 | 0.3375 | 0.5625 | 2.344% | 0.13393 | 1.052% | 82% | 3500 | 242.1878 | 4.7663 | 0.1968 | 5.8125 | 24% | 38.701 | -133.7389
INSTITUTIONAL
High water use hospital (inpatient)
Low water use hospital (outpatient)
Assembly & educational
Note on H4: User Note: Assumes the building is 4 sided
Note on Q4: Eric Chisholm: Wall area (m2) x [Heating Degree Days (K * days /yr) + (Cooling Degree Days (K * days /yr)] x 24 (hrs/day) / Insulation RSI (m2 * K / W) / 277778 Wh / GJ = GJ/yr
Note on AE14: User Note: This unitary cost was not originally specified and uses the same unitary cost as a High-Rise Hotel.
Note on AE17: User Note: This unitary cost was not originally specified and uses the same unitary cost as a High-Rise Hotel.
Note on M27: User Note: The methodology assumes the insulation area is flat (attic blown insulation), not rigid insulation against the sloped roof.
Note on A30: User Note: This row is not used in this tab - no formulas are included in this row
Note on A31: User Note: This row is not used in this tab - no formulas are included in this row
Note on A32: User Note: This row is not used in this tab - no formulas are included in this row
Note on A33: User Note: This row is not used in this tab - no formulas are included in this row